## 1) User Guide and Network Maps
User Guide
With this tool we aim to provide our customers with information on where there is spare capacity for new developments to connect to our network without triggering reinforcement work. To aid our customers in interpreting the information contained within this tool we have produced a user guide which can be found below. Please note that the data presented in this tool is based on high level analysis and as such may differ from the results of a formal connection application. If your proposed development falls within an area with limited network capacity please contact us to discuss a possible solution. We will always to work with customers to overcome network constraints whether this is through traditional reinforcement or smart network solutions.
Map Data
We now publish an interactive map on our website that contains the same information as contained within this tool.
Click here to access the map.
| Last Updated* | 2023-05-24
This version is 1 day old
* due to the infrequency of EHV plant replacement, switchgear ratings are checked quarterly
| Switchgear ratings checked | 2023-02-28
This version is 85 days old

## 2) 11 kV & 6.6 kV Connections
11 kV & 6.6 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab. Please note that the value of headroom quoted by this tool is based on total capacity available for new connections, the column beside it shows the maximum size of a single connection, based on the on-site primary switchgear rating, which can be much lower. To reflect this the 'Can Connect?' RAG value is derived using the lowest of these two values. It is normally not possible to accommodate a single connection of more than 7 MW at 11 kV or 6.6 kV, this is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations. It is possible that due to these addtional factors and the point of connection requested that the maximum connection size is lower than the values shown below.
Inputs | [18 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest primary substations to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. The results are based on both local constraints and constraints at the associated BSP. | [10 empty] | RAG | Limiting factor: Headroom |  | Limiting factor: Switchgear rating
Northing |  | Enter Data | [17 empty] | Capacity <90% of headroom |  | Suitable
Capacity (MW) |  | Enter Data | [17 empty] | Capacity >90% & < 100% of headroom |  | N/A
Connection Type |  | Enter Data | [17 empty] | Capacity >100% of headroom |  | Unsuitable
Distribution Network Capacity Capacity | [18 empty] | Transmission Constraints (App G)
No | Distance (km) | Primary Substation |  |  | BSP Group |  |  | BCA Group (GSP) |  |  | Primary Substation Location |  | Headroom (MW) | Max Single circuit connection (MW) |  | Can Connect? (RAG) | Can Connect? (RAG) | Limiting factor | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[11 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network through step up transformers.
Generation Synchronous (HV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network directly i.e. without step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 3) 33 kV Connections
33 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab.
Please note that the value of headroom quoted by this tool is based on total capacity available for new connections not the maximum size of a single connection which can be much lower. It is normally not possible to accommodate a single connection of more than 40 MW at 33 kV. This is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations.
Inputs | [11 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest BSP to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. It should be noted that the network assets surrounding your site may not be fed from the closest BSP. |  |  |  |  | Capacity <90% of headroom
Northing |  | Enter Data | [10 empty] | Capacity >90% & < 100% of headroom
Capacity (MW) |  | Enter Data | [10 empty] | Capacity >100% of headroom
Connection Type |  | Enter Data
Distribution Network Capacity Capacity | [11 empty] | Transmission Constraints (App G)
No | Distance (km) | BSP |  |  | BCA Group (GSP) |  |  | BSP Location |  | Headroom (MW) | Can Connect? (RAG) | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[8 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the EHV network through step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 4) Primary Headroom Data
Primary Substation Headroom
Primary Substation | Voltage (kV) | BSP Group |  | BCA Group (GSP) | Primary Substation Location |  | Individual Circuit Capacity |  | Demand Headroom (MW) |  | Generation Headroom N-0 -(MW) |  |  | Battery Storage Headroom N-0 -(MW)
[5 empty] | Easting | Northing | CB Rating | MVA | Firm | N-0 | Inverter Based | Synchronous - LV | Synchronous - HV
ALBION ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367434 | 426087 | 400 | 4.5726 | 2.1176 | 13.0168 | 31.8769 | 5.5624 | 4.0761 | 13.0168 | 0 | 0 | Data submitted, clock started 02/03/2023
ALDERLEY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385044 | 379026 | 400 | 7.621 | 10.6064 | 17.2964 | 4.38 | 1.6977 | 1.4038 | 4.38 | 1.4344 | 5.768 | Offer now with ENW, due to be signed 16/08/2023
ALSTON | 11 | PENRITH & SHAP | PENRITH | HUTTON | 372125 | 546499 | 400 | 7.621 | 0.0053476 | 1.3053 | 3.3047 | 3.3047 | 3.3047 | 1.3053 | 3.2626 | 1.1073 | Awaiting payment for Hutton schemes
AMBLESIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 337602 | 503506 | 400 | 7.621 | 8.0287 | 17.2287 | 29.6287 | 25.3128 | 18.1928 | 17.2287 | 0 | 0 | Awaiting payment for Hutton schemes
ANCOATS NORTH T11 & T12 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385022 | 398830 | 400 | 4.5726 | 6.679 | 10.816 | 32.3302 | 6.5658 | 4.7906 | 10.816 | 4.8939 | 0.33304 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
ANCOATS NORTH T14 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385032 | 398840 | 400 | 4.5726 | 7.4803 | 12.2303 | 19.2839 | 19.2839 | 15.7367 | 12.2303 | 15.7536 | 7.6053 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
ANNIE PIT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300011 | 527810 | 400 | 7.621 | 4.6556 | 10.1556 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed, returned on 11/04/23
ANSDELL | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 334416 | 428229 | 800 | 9.1452 | 0 | 0 | 19.8677 | 9.7864 | 7.1405 | 0 | 0 | 0 | Offer signed, return on 14/03/23
ARDWICK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384753 | 397415 | 630 | 7.2019 | 2.7998 | 7.7998 | 11.2179 | 1.9575 | 1.4344 | 7.7998 | 1.4344 | 0 | N/A
ARNSIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 346495 | 478180 | 400 | 7.621 | 10.6465 | 13.4313 | 18.3845 | 18.3845 | 18.3845 | 13.4313 | 0 | 0 | Awaiting payment for Hutton schemes
ASHTON (GOLBORNE) | 6.6 | ORRELL | ORRELL | WASHWAY FARM / KIRKBY | 357056 | 400663 | 800 | 9.1452 | 0 | 5.1664 | 26.2485 | 8.7327 | 6.3717 | 5.1664 | 5.9845 | 2.5354 | #N/A
ASHTON (RIBBLE) | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 350275 | 430526 | 630 | 7.2019 | 1.236 | 1.236 | 5.57 | 1.9575 | 1.4344 | 1.236 | 1.4344 | 0 | Offer signed, return on 14/03/23
ASHTON ON MERSEY | 6.6 | SALE | SALE | CARRINGTON | 377188 | 392252 | 630 | 7.2019 | 9.9787 | 14.1187 | 28.8941 | 8.8533 | 6.4596 | 14.1187 | 6.5315 | 13.4847 | N/A
ASHTON UNDER LYNE T11 & T12 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393275 | 399319 | 630 | 7.2019 | 5.7709 | 9.9079 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | N/A
ASHTON UNDER LYNE T13 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393285 | 399329 | 630 | 7.2019 | 6.9141 | 11.6641 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | N/A
ASHWOOD DALE | 6.6 | BUXTON | BUXTON | STALYBRIDGE | 406537 | 373050 | 630 | 7.2019 | 5.2612 | 12.5422 | 31.4391 | 8.7775 | 6.4043 | 12.5422 | 1.3561 | 10.6051 | N/A
ASKAM | 11 | ULVERSTON | ULVERSTON | HARKER | 321558 | 477806 | 630 | 12.0031 | 1.548 | 8.528 | 11.7207 | 7.8316 | 5.6287 | 8.528 | 6.4697 | 8.428 | Offer signed, returned on 11/04/23
ASKERTON CASTLE | 11 | - | - | HARKER | 354779 | 568913 | 800 | 15.242 | 0.92953 | 1.6295 | 3.9789 | 3.9789 | 3.9789 | 1.6295 | 3.9789 | 1.6295 | Offer signed, returned on 11/04/23
ASPATRIA | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 314417 | 542840 | 400 | 7.621 | 4.044 | 6.044 | 7 | 1.9575 | 1.4344 | 6.044 | 0 | 0 | Offer signed, returned on 11/04/23
ATHERTON TOWN CENTRE | 11 | ATHERTON | ATHERTON | KEARSLEY | 367546 | 403338 | 800 | 15.242 | 7.424 | 19.184 | 29.909 | 4.9243 | 3.5392 | 19.184 | 3.7461 | 0 | Offer signed, returned on 18/04/23
ATHLETIC ST | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385381 | 432208 | 400 | 4.5726 | 7.5714 | 11.0714 | 22.71 | 13.416 | 9.7886 | 11.0714 | 9.6723 | 7.1892 | Data submitted, clock started 02/03/2023
AVENHAM | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 354028 | 429192 | 800 | 9.1452 | 2.1449 | 2.1449 | 11.2179 | 1.9575 | 1.4344 | 2.1449 | 1.4344 | 0 | Offer signed, return on 14/03/23
BAGULEY | 11 | SALE | SALE | CARRINGTON | 380562 | 389035 | 400 | 7.621 | 4.9908 | 9.6278 | 30.0013 | 10.0594 | 7.2299 | 9.6278 | 7.6584 | 8.6278 | N/A
BAMBER BRIDGE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 356431 | 426698 | 630 | 12.0031 | 4.5313 | 8.6683 | 11.2179 | 1.9575 | 1.4344 | 8.6683 | 1.4344 | 10.2623 | Offer signed, return on 14/03/23
BARBARA ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370695 | 407609 | 630 | 7.2019 | 0 | 3.6925 | 11.2179 | 1.9575 | 1.4344 | 3.6925 | 1.4344 | 9.8525 | Offer signed, returned on 18/04/23
BARROW | 11 | BARROW & SANDGATE | BARROW | HARKER | 319709 | 470489 | 630 | 12.0031 | 13.8644 | 18.3644 | 29.0331 | 11.9089 | 8.5592 | 18.3644 | 8.0292 | 18.3194 | Offer signed, returned on 11/04/23
BARTON DOCK RD | 6.6 | BARTON | BARTON | CARRINGTON | 378864 | 395534 | 630 | 7.2019 | 2.9651 | 9.2151 | 11.2179 | 1.9575 | 1.4344 | 9.2151 | 1.4344 | 10.2441 | N/A
BEDFORD | 11 | ATHERTON | ATHERTON | KEARSLEY | 366258 | 399876 | 800 | 15.242 | 5.1873 | 9.6873 | 28.5003 | 10.2252 | 7.3491 | 9.6873 | 7.2768 | 0 | Offer signed, returned on 18/04/23
BELGRAVE | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393008 | 403366 | 630 | 7.2019 | 7.9635 | 11.4635 | 23.9216 | 13.012 | 9.4939 | 11.4635 | 9.5768 | 4.6017 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
BENCHILL | 11 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382454 | 388020 | 400 | 7.621 | 7.8921 | 9.8921 | 11.2179 | 1.9575 | 1.4344 | 9.8921 | 1.4344 | 9.8921 | Offer now with ENW, due to be signed 16/08/2023
BENTHAM | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 366887 | 470130 | 400 | 7.621 | 0.7818 | 5.2818 | 7.259 | 7.259 | 7.259 | 5.2818 | 0 | 0 | Awaiting payment for Hutton schemes
BISPHAM | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331655 | 439667 | 630 | 7.2019 | 5.6529 | 10.2899 | 11.2179 | 1.9575 | 1.4344 | 10.2899 | 1.4344 | 10.1499 | Offer signed, return on 14/03/23
BLACKBULL | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353041 | 433005 | 630 | 7.2019 | 7.0984 | 11.2354 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 6.4123 | Offer signed, return on 14/03/23
BLACKBURN | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 370584 | 429294 | 400 | 4.5726 | 8.9808 | 13.6178 | 31.3792 | 8.7973 | 6.4187 | 13.6178 | 6.1854 | 10.7604 | Offer signed, return on 14/03/23
BLACKFRIARS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383030 | 399104 | 630 | 7.2019 | 0 | 10.8794 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed, returned on 18/04/23
BLACKLEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 383882 | 403258 | 630 | 7.2019 | 11.043 | 15.68 | 30.3333 | 13.6743 | 9.9771 | 15.68 | 9.7958 | 15.68 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
BLACKPOOL | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330835 | 435308 | 630 | 7.2019 | 12.671 | 20.421 | 33.7019 | 9.0499 | 6.603 | 20.421 | 6.7082 | 17.439 | Offer signed, return on 14/03/23
BOLLINGTON | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 393042 | 377873 | 630 | 12.0031 | 1.0768 | 3.4991 | 11.2179 | 1.9575 | 1.4344 | 3.4991 | 1.4344 | 0 | N/A
BOLTON BY BOWLAND | 11 | PADIHAM | PADIHAM | PADIHAM | 378320 | 449559 | 400 | 7.621 | 0 | 4.3635 | 8.4802 | 8.4802 | 8.4802 | 4.3635 | 8.4802 | 3.8465 | Data Submitted, clock start due 27/05/23
BOLTON LE SANDS | 11 | LANCASTER | LANCASTER | HEYSHAM | 347707 | 467237 | 400 | 7.621 | 5.8485 | 9.3485 | 24.8162 | 4.6774 | 3.4275 | 9.3485 | 1.5151 | 5.0572 | Data submitted, clock start due 02/03/2023
BOTANY BAY | 11 | LEYLAND | LEYLAND | PENWORTHAM | 359442 | 418850 | 630 | 12.0031 | 1.9979 | 9.9979 | 20.5557 | 20.5557 | 19.2127 | 9.9979 | 19.2177 | 9.8578 | Offer signed, return on 14/03/23
BOW LANE | 11 | LEYLAND | LEYLAND | PENWORTHAM | 354895 | 422392 | 400 | 7.621 | 4.6679 | 9.3049 | 29.2513 | 6.2455 | 4.4887 | 9.3049 | 3.7567 | 5.6289 | Offer signed, return on 14/03/23
BOWATERS | 11 | BARROW & SANDGATE | BARROW | HARKER | 319579 | 472480 | 400 | 7.621 | 13.8459 | 34.3459 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | Offer signed, returned on 11/04/23
BOWDON | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376743 | 386810 | 400 | 7.621 | 6.5909 | 11.2279 | 32.4374 | 12.448 | 8.9467 | 11.2279 | 8.9022 | 10.8219 | N/A
BRADFORD | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387613 | 397710 | 400 | 4.5726 | 8.4381 | 13.0751 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | N/A
BRADSHAWGATE | 6.6 | BOLTON | BOLTON | KEARSLEY | 371891 | 408910 | 400 | 4.5726 | 10.6025 | 21.2425 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed, returned on 18/04/23
BRAMHALL | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 389440 | 386463 | 630 | 12.0031 | 4.9884 | 8.4884 | 24.6012 | 12.4312 | 8.9345 | 8.4884 | 9.1136 | 8.37 | Offer signed, returned on 18/04/23
BRIDGEWATER | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383543 | 397628 | 800 | 9.1452 | 7.7665 | 14.7665 | 30.3079 | 12.9422 | 9.443 | 14.7665 | 9.8568 | 6.6125 | Offer now with ENW, due to be signed 16/08/2023
BRINKSWAY | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 388434 | 389885 | 400 | 4.5726 | 8.7353 | 13.907 | 30.1118 | 13.0359 | 9.5114 | 13.907 | 9.4256 | 12.706 | Offer signed, returned on 18/04/23
BROADHEATH | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376412 | 389026 | 400 | 7.621 | 14.2555 | 19.4806 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | N/A
BROADWAY | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 344792 | 464471 | 630 | 7.2019 | 11.9995 | 16.1365 | 26.0396 | 4.6774 | 3.4275 | 16.1365 | 1.5151 | 5.0572 | Data submitted, clock start due 02/03/2023
BUCKSHAW | 11 | LEYLAND | LEYLAND | PENWORTHAM | 356748 | 421312 | 630 | 12.0031 | 10.9393 | 15.4393 | 27.8355 | 13.8265 | 9.9373 | 15.4393 | 9.8081 | 10.2615 | Offer signed, return on 14/03/23
BURNLEY | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385569 | 434469 | 400 | 4.5726 | 15.7345 | 15.7345 | 15.2123 | 5.7083 | 4.165 | 15.2123 | 3.8058 | 9.6649 | Data submitted, clock started 02/03/2023
BURNLEY CENTRE | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384308 | 432288 | 630 | 7.2019 | 9.7989 | 9.7989 | 23.2074 | 9.794 | 7.146 | 9.7989 | 6.7909 | 5.3989 | Data submitted, clock started 02/03/2023
BURNLEY NORTH | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384418 | 434168 | 630 | 7.2019 | 1.1542 | 10.1542 | 17.9015 | 17.9015 | 17.3445 | 10.1542 | 17.1739 | 8.8706 | Data submitted, clock started 02/03/2023
BURROW BECK | 11 | LANCASTER | LANCASTER | HEYSHAM | 347903 | 458401 | 630 | 12.0031 | 6.3234 | 10.8234 | 10.1139 | 1.6652 | 1.1968 | 10.1139 | 0.7451 | 5.0572 | Data submitted, clock start due 02/03/2023
BURSCOUGH BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344595 | 412486 | 630 | 12.0031 | 4.7287 | 7.8902 | 15.5363 | 8.603 | 6.1831 | 7.8902 | 4.4683 | 2.8737 | Offer signed, return on 14/03/23
BURY TOWN CENTRE | 6.6 | BURY | BURY | KEARSLEY | 380863 | 410807 | 400 | 4.5726 | 8.2754 | 12.4124 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 8.2958 | Offer signed, returned on 18/04/23
BUSHELL ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353809 | 430094 | 400 | 4.5726 | 5.7554 | 9.8954 | 11.2179 | 1.9575 | 1.4344 | 9.8954 | 1.4344 | 9.8954 | Offer signed, return on 14/03/23
CAMPBELL ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372937 | 406428 | 630 | 12.0031 | 6.3133 | 9.8133 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 5.9733 | Offer signed, returned on 18/04/23
CANNON ST | 6.6 | RED BANK | RED BANK | WHITEGATE | 384064 | 398635 | 400 | 4.5726 | 14.8503 | 35.8503 | 0.45991 | 0.074591 | 0.054424 | 0.45991 | 0.16545 | 1.3982 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
CAPONTREE | 11 | CARLISLE | CARLISLE | HARKER | 352906 | 559671 | 400 | 7.621 | 15.0903 | 18.0693 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed, returned on 11/04/23
CARLETON | 11 | EGREMONT | EGREMONT | HARKER | 308796 | 498305 | 630 | 12.0031 | 3.0554 | 5.5554 | 8.424 | 8.424 | 8.424 | 5.5554 | 8.424 | 5.5206 | Offer signed, returned on 11/04/23
CARLISLE NORTH | 11 | - | - | HARKER | 338547 | 560280 | 630 | 12.0031 | 11.3849 | 31.8849 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offer signed, returned on 11/04/23
CARR ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376984 | 401329 | 400 | 7.621 | 9.9331 | 14.0701 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed, returned on 18/04/23
CASTLETON | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 388461 | 411290 | 630 | 7.2019 | 6.2193 | 10.8563 | 23.3483 | 3.7868 | 2.7629 | 10.8563 | 2.09 | 9.5109 | Data submitted, clock started 02/03/2023
CATTERALL WATERWORKS | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349381 | 442178 | 400 | 4.5726 | 0 | 0 | 9.5568 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed, return on 14/03/23
CECIL ST | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 331301 | 437023 | 630 | 7.2019 | 10.8561 | 16.0461 | 30.7725 | 16.5646 | 12.086 | 16.0461 | 12.1148 | 12.9781 | Offer signed, return on 14/03/23
CENTRAL MANCHESTER | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384852 | 397718 | 630 | 7.2019 | 15.3358 | 24.3358 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | N/A
CHADDERTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389161 | 403872 | 400 | 4.5726 | 14.6326 | 20.6326 | 28.7732 | 4.6666 | 3.4049 | 20.6326 | 1.3649 | 0 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
CHAMBERHALL | 6.6 | BURY | BURY | KEARSLEY | 380280 | 411215 | 600 | 6.8589 | 3.4081 | 8.7281 | 11.2179 | 1.9575 | 1.4344 | 8.7281 | 1.4344 | 8.4761 | Offer signed, returned on 18/04/23
CHAPEL WHARF | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383499 | 398634 | 630 | 7.2019 | 0 | 15.7641 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed, returned on 18/04/23
CHASSEN RD | 6.6 | BARTON | BARTON | CARRINGTON | 375542 | 394453 | 630 | 7.2019 | 2.4832 | 13.3832 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | N/A
CHATSWORTH ST | 11 | BARROW & SANDGATE | BARROW | HARKER | 319188 | 470003 | 800 | 15.242 | 7.6325 | 15.0325 | 31.5852 | 10.2922 | 7.3972 | 15.0325 | 7.3076 | 14.6753 | Offer signed, returned on 11/04/23
CHEADLE HEATH | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 387062 | 389054 | 630 | 7.2019 | 4.9776 | 8.4776 | 22.4112 | 11.1959 | 8.1689 | 8.4776 | 8.0328 | 8.3048 | Offer signed, returned on 18/04/23
CHEADLE HULME | 11 | ADSWOOD | ADSWOOD | BREDBURY | 387386 | 386308 | 630 | 12.0031 | 8.086 | 12.723 | 31.3411 | 13.0441 | 9.3751 | 12.723 | 9.2691 | 12.9036 | Offer signed, returned on 18/04/23
CHEETHAM HILL | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 383606 | 402218 | 400 | 4.5726 | 3.0639 | 3.0639 | 22.1947 | 15.5641 | 11.356 | 3.0639 | 11.1639 | 2.7039 | Offer signed, returned on 18/04/23
CHELFORD | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 382184 | 373490 | 400 | 7.621 | 10.6064 | 17.2964 | 4.38 | 1.6977 | 1.4038 | 4.38 | 1.4344 | 5.768 | Offer now with ENW, due to be signed 16/08/2023
CHESTER RD T11 & T12 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381030 | 396165 | 630 | 7.2019 | 3.9535 | 8.9535 | 24.4081 | 8.005 | 5.8407 | 8.9535 | 5.9831 | 2.9543 | Offer now with ENW, due to be signed 16/08/2023
CHESTER RD T13 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381040 | 396175 | 630 | 7.2019 | 8.6031 | 13.9049 | 18.6656 | 18.6656 | 17.1439 | 13.9049 | 17.154 | 12.6129 | Offer now with ENW, due to be signed 16/08/2023
CHORLEY SOUTH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358658 | 417041 | 800 | 15.242 | 2.0232 | 5.5232 | 24.012 | 13.2151 | 9.498 | 5.5232 | 5.1053 | 5.0492 | Offer signed, return on 14/03/23
CHORLTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 381411 | 393754 | 400 | 4.5726 | 3.2837 | 9.2837 | 11.2179 | 1.9575 | 1.4344 | 9.2837 | 1.4344 | 9.12 | Offer now with ENW, due to be signed 16/08/2023
CHURCH | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374687 | 428919 | 800 | 9.1452 | 0.96841 | 11.9684 | 18.6892 | 18.6892 | 17.1498 | 11.9684 | 7.0436 | 11.2916 | Data Submitted, clock start due 27/05/23
CLARENDON RD | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369051 | 429883 | 400 | 4.5726 | 9.8233 | 14.4603 | 26.0405 | 5.5413 | 4.0431 | 14.4603 | 2.9125 | 3.9899 | Offer signed, return on 14/03/23
CLAUGHTON | 11 | LANCASTER | LANCASTER | HEYSHAM | 355872 | 466268 | 630 | 12.0031 | 0.34681 | 3.8468 | 8.4614 | 4.6774 | 3.4275 | 3.8468 | 1.5151 | 3.7068 | Data submitted, clock start due 02/03/2023
BLACKBURN RD CLAYTON | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374632 | 430529 | 630 | 7.2019 | 11.6258 | 19.3058 | 27.6988 | 10.9839 | 8.0141 | 19.3058 | 7.0436 | 19.3058 | Data Submitted, clock start due 27/05/23
CLEVELEYS | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 332286 | 443104 | 630 | 7.2019 | 4.5751 | 8.0751 | 11.2179 | 1.9575 | 1.4344 | 8.0751 | 1.4344 | 7.8631 | Offer signed, return on 14/03/23
CLIFTON JUNCTION | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 379289 | 403073 | 630 | 12.0031 | 6.1475 | 9.6475 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 4.7605 | Offer signed, returned on 18/04/23
CLOVER HILL | 6.6 | NELSON | NELSON | PADIHAM | 386638 | 437064 | 630 | 7.2019 | 9.2209 | 18.1261 | 0 | 0 | 0 | 0 | 0 | 0 | Data Submitted, clock start due 27/05/23
COG LANE | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 382462 | 432232 | 800 | 9.1452 | 6.5036 | 16.9285 | 43.3786 | 9.7476 | 7.1121 | 16.9285 | 1.845 | 13.1837 | Data Submitted, clock start due 27/05/23
CONISTON | 11 | ULVERSTON | ULVERSTON | HARKER | 329874 | 497641 | 400 | 7.621 | 0 | 1.4823 | 4.8516 | 4.8516 | 4.8516 | 1.4823 | 4.8516 | 1.4303 | Offer signed, returned on 11/04/23
COPSE RD | 6.6 | THORNTON | THORNTON | STANAH | 333013 | 446934 | 630 | 7.2019 | 5.9089 | 7.5459 | 23.0632 | 5.4114 | 3.9483 | 7.5459 | 2.296 | 3.1319 | N/A
COX GREEN | 11 | BOLTON | BOLTON | KEARSLEY | 371893 | 413641 | 630 | 12.0031 | 4.3613 | 8.6613 | 11.2179 | 1.9575 | 1.4344 | 8.6613 | 1.4344 | 8.1583 | Offer signed, returned on 18/04/23
CRAGGS ROW | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353740 | 430080 | 630 | 7.2019 | 5.7554 | 9.8954 | 11.2179 | 1.9575 | 1.4344 | 9.8954 | 1.4344 | 9.0804 | Offer signed, return on 14/03/23
CROWN LANE | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 362706 | 410859 | 400 | 7.621 | 3.0684 | 7.7054 | 32.4077 | 7.4513 | 5.3554 | 7.7054 | 0.088852 | 0 | Offer signed, returned on 18/04/23
CULCHETH | 11 | GOLBORNE | GOLBORNE | BOLD | 365430 | 395366 | 400 | 7.621 | 2.5713 | 8.5713 | 19.8861 | 12.6568 | 9.2748 | 8.5713 | 0 | 0 | N/A
CUTACRE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 369848 | 404515 | 630 | 12.0031 | 17.521 | 22.4568 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed, returned on 18/04/23
DALTON | 11 | ULVERSTON | ULVERSTON | HARKER | 323582 | 474255 | 400 | 7.621 | 1.548 | 9.028 | 32.4628 | 16.015 | 11.5103 | 9.028 | 11.6712 | 8.928 | Offer signed, returned on 11/04/23
DEANSGATE | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383463 | 398149 | 630 | 7.2019 | 10.4224 | 17.7524 | 29.9539 | 12.4441 | 9.0796 | 17.7524 | 9.1618 | 11.3246 | Offer now with ENW, due to be signed 16/08/2023
DENTON EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 392394 | 395626 | 630 | 7.2019 | 10.6363 | 15.2733 | 29.02 | 5.2662 | 3.859 | 15.2733 | 1.4344 | 11.2179 | N/A
DENTON WEST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390380 | 395565 | 400 | 4.5726 | 6.5168 | 11.1538 | 30.1795 | 5.2662 | 3.859 | 11.1538 | 1.4344 | 11.2179 | N/A
DICKINSON ST | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 384109 | 397722 | 800 | 9.1452 | 8.7594 | 8.7594 | 36.7251 | 12.459 | 9.0905 | 8.7594 | 9.5067 | 5.4068 | Offer now with ENW, due to be signed 16/08/2023
DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384792 | 391153 | 630 | 7.2019 | 8.7729 | 13.4099 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer now with ENW, due to be signed 16/08/2023
DODGSON RD | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 355190 | 430397 | 400 | 4.5726 | 2.1449 | 2.1449 | 11.2179 | 1.9575 | 1.4344 | 2.1449 | 1.4344 | 0 | Offer signed, return on 14/03/23
DOUGLAS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352220 | 429932 | 400 | 4.5726 | 9.1631 | 15.8231 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed, return on 14/03/23
DROYLSDEN EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390532 | 398053 | 630 | 7.2019 | 7.2227 | 11.8597 | 30.1795 | 5.2662 | 3.859 | 11.8597 | 1.4344 | 9.4097 | N/A
DUKINFIELD | 6.6 | HYDE | HYDE | STALYBRIDGE | 394372 | 396438 | 400 | 4.5726 | 11.2867 | 15.9237 | 25.1126 | 4.0729 | 2.9717 | 15.9237 | 2.6715 | 15.6217 | N/A
DUMERS LANE | 11 | BURY | BURY | KEARSLEY | 380057 | 408141 | 400 | 7.621 | 8.1185 | 14.6185 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 7.2779 | Offer signed, returned on 18/04/23
DUMPLINGTON | 11 | BARTON | BARTON | CARRINGTON | 376770 | 397157 | 800 | 15.242 | 21.6916 | 23.0916 | 10.6869 | 1.7595 | 1.2646 | 10.6869 | 0.99981 | 8.4492 | N/A
EASTLANDS | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386458 | 398693 | 800 | 9.1452 | 10.1778 | 14.8148 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
EASTON | 11 | - | - | HARKER | 343201 | 571738 | 800 | 15.242 | 0 | 0.23073 | 2.8786 | 2.8786 | 2.8786 | 0.23073 | 2.8786 | 0 | Offer signed, returned on 11/04/23
EGREMONT | 11 | EGREMONT | EGREMONT | HARKER | 301070 | 513074 | 400 | 7.621 | 2.6903 | 5.1903 | 21.2377 | 17.3897 | 12.4984 | 5.1903 | 12.6319 | 4.995 | Offer signed, returned on 11/04/23
EMBLETON | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 315767 | 529389 | 400 | 7.621 | 3.2358 | 14.9938 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed, returned on 11/04/23
EXCHANGE ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369100 | 423028 | 800 | 9.1452 | 2.1176 | 9.2237 | 23.5705 | 5.5624 | 4.0761 | 9.2237 | 0 | 0 | Data submitted, clock started 02/03/2023
FAILSWORTH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389631 | 401496 | 400 | 4.5726 | 8.4366 | 13.0736 | 28.9569 | 9.2058 | 6.7459 | 13.0736 | 1.3649 | 0 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
FALLOWFIELD | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 385608 | 393881 | 400 | 4.5726 | 7.3452 | 11.9822 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2006 | Offer now with ENW, due to be signed 16/08/2023
FARNWORTH | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373726 | 405532 | 800 | 15.242 | 7.3008 | 11.3008 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed, returned on 18/04/23
FENISCOWLES | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 364660 | 425120 | 630 | 7.2019 | 2.1176 | 13.8689 | 19.0252 | 5.5624 | 4.0761 | 13.8689 | 0 | 0 | Data submitted, clock started 02/03/2023
FERODO | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 405720 | 381338 | 630 | 12.0031 | 1.6218 | 14.3912 | 30.4491 | 14.891 | 10.7024 | 14.3912 | 11.2192 | 5.6473 | N/A
FLAT LANE | 11 | PADIHAM | NELSON | PADIHAM | 383248 | 456995 | 630 | 12.0031 | 0 | 5.2771 | 11.0501 | 11.0501 | 11.0501 | 5.2771 | 11.0501 | 4.4257 | Data Submitted, clock start due 27/05/23
FREDERICK RD | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381697 | 399348 | 800 | 9.1452 | 0 | 12.4039 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed, returned on 18/04/23
FUSEHILL | 11 | CARLISLE | CARLISLE | HARKER | 341042 | 555452 | 400 | 7.621 | 3.1815 | 9.6815 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed, returned on 11/04/23
GALE | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 389570 | 414943 | 400 | 4.5726 | 12.1782 | 16.8152 | 30.4947 | 12.1354 | 8.8543 | 16.8152 | 8.6697 | 0 | Data submitted, clock started 02/03/2023
GARSTANG | 6.6 | THORNTON | THORNTON | STANAH | 348319 | 445221 | 630 | 7.2019 | 1.0849 | 1.0849 | 14.6333 | 13.1145 | 9.6102 | 1.0849 | 9.0987 | 0.2593 | N/A
GATLEY | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384242 | 388388 | 400 | 4.5726 | 1.4591 | 11.9591 | 4.38 | 1.6977 | 1.4038 | 4.38 | 1.4344 | 5.768 | Offer now with ENW, due to be signed 16/08/2023
GIDLOW | 6.6 | WIGAN | WIGAN | KIRKBY | 357620 | 406662 | 400 | 4.5726 | 3.7928 | 8.4298 | 32.1414 | 12.2022 | 8.9031 | 8.4298 | 8.9257 | 9.6892 | Data submitted for next PP. Awaiting clock start date
GILLSROW | 11 | PENRITH & SHAP | PENRITH | HUTTON | 337117 | 526444 | 630 | 12.0031 | 1.3336 | 3.5336 | 7.5611 | 7.5611 | 7.5611 | 3.5336 | 7.4769 | 2.881 | Awaiting payment for Hutton schemes
GLAXO | 11 | ULVERSTON | ULVERSTON | HARKER | 330458 | 477825 | 400 | 7.621 | 6.4012 | 18.3512 | 12.1475 | 2 | 1.4374 | 12.1475 | 1.4212 | 12.0107 | Offer signed, returned on 11/04/23
GLOSSOP | 11 | HYDE | HYDE | STALYBRIDGE | 402300 | 394074 | 630 | 12.0031 | 8.2116 | 12.8486 | 31.2376 | 7.5812 | 5.5554 | 12.8486 | 5.4751 | 12.055 | N/A
GOLBORNE | 11 | GOLBORNE | GOLBORNE | BOLD | 360621 | 397766 | 800 | 15.242 | 3.4508 | 8.9508 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | N/A
GOWHOLE | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 401104 | 383846 | 400 | 7.621 | 5.2669 | 9.9039 | 29.9812 | 10.4107 | 7.4823 | 9.9039 | 7.0494 | 5.6473 | N/A
GRANE RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378312 | 422726 | 400 | 4.5726 | 9.2872 | 14.3872 | 24.7332 | 8.4598 | 6.1725 | 14.3872 | 5.885 | 14.3872 | Data Submitted, clock start due 27/05/23
GRANGE | 11 | ULVERSTON | ULVERSTON | HARKER | 340240 | 478314 | 400 | 7.621 | 4.9133 | 10.9133 | 21.0097 | 21.0097 | 19.5815 | 10.9133 | 19.5311 | 10.7263 | Offer signed, returned on 11/04/23
GREAT HARWOOD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373765 | 431955 | 630 | 7.2019 | 9.8983 | 18.0183 | 19.4454 | 3.9293 | 2.8669 | 18.0183 | 1.1085 | 9.368 | Data Submitted, clock start due 27/05/23
GREEN LANE (ALTRINCHAM) | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 378744 | 387772 | 400 | 7.621 | 5.7453 | 10.3823 | 32.2668 | 15.6287 | 11.2327 | 10.3823 | 11.1508 | 10.8283 | N/A
GREEN LANE (HAZEL GROVE) | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 391570 | 387132 | 400 | 7.621 | 0 | 3.9671 | 33.5043 | 7.5903 | 5.4553 | 3.9671 | 5.6166 | 0.45951 | Offer signed, returned on 18/04/23
GREEN ST T11 | 6.6 | WIGAN | WIGAN | KIRKBY | 358235 | 404898 | 630 | 7.2019 | 0.37616 | 4.3762 | 21.3921 | 9.2418 | 6.7431 | 4.3762 | 4.1968 | 3.8848 | Data submitted for next PP. Awaiting clock start date
GREEN ST T12 & T13 | 6.6 | WIGAN | WIGAN | KIRKBY | 358225 | 404888 | 630 | 7.2019 | 5.0031 | 10.5431 | 32.3774 | 7.8145 | 5.7017 | 10.5431 | 5.7981 | 10.2071 | Data submitted for next PP. Awaiting clock start date
GREENFIELD | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 399322 | 404583 | 800 | 15.242 | 12.5934 | 17.0934 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | N/A
GREENHILL | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393262 | 404755 | 400 | 4.5726 | 15.9878 | 28.2673 | 55.5263 | 10.1233 | 7.3863 | 28.2673 | 6.8407 | 4.6017 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
GRIFFIN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367171 | 427130 | 800 | 9.1452 | 2.1176 | 13.4175 | 28.6318 | 5.5624 | 4.0761 | 13.4175 | 0 | 0 | Data submitted, clock started 02/03/2023
HADFIELD | 11 | HYDE | HYDE | STALYBRIDGE | 401790 | 395876 | 400 | 7.621 | 12.23 | 16.9503 | 6.2189 | 1.0239 | 0.73589 | 6.2189 | 0.83754 | 7.0779 | N/A
HALL CROSS | 6.6 | PEEL | PEEL | PENWORTHAM | 342288 | 430650 | 630 | 7.2019 | 2.1727 | 2.1727 | 2.4151 | 2.4151 | 2.4151 | 2.1727 | 0 | 0 | Offer signed, return on 14/03/23
HANDFORTH | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385958 | 383397 | 400 | 7.621 | 11.0459 | 15.6829 | 4.38 | 1.6977 | 1.4038 | 4.38 | 1.4344 | 5.768 | Offer now with ENW, due to be signed 16/08/2023
HANGING BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 346186 | 417486 | 630 | 12.0031 | 1.7129 | 5.7129 | 10.8975 | 10.8975 | 10.5469 | 5.7129 | 5.1053 | 5.1053 | Offer signed, return on 14/03/23
HAREHOLME | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 382535 | 422283 | 800 | 9.1452 | 5.7899 | 10.4269 | 31.6811 | 13.017 | 9.4976 | 10.4269 | 9.5452 | 9.9239 | Data Submitted, clock start due 27/05/23
HARPURHEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 385907 | 402469 | 400 | 4.5726 | 11.192 | 15.832 | 30.4539 | 12.6666 | 9.2419 | 15.832 | 9.1946 | 15.552 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
HARWOOD | 11 | BOLTON | BOLTON | KEARSLEY | 374043 | 410941 | 400 | 7.621 | 3.012 | 7.312 | 11.2179 | 1.9575 | 1.4344 | 7.312 | 1.4344 | 7.187 | Offer signed, returned on 18/04/23
HATTERSLEY | 11 | HYDE | HYDE | STALYBRIDGE | 398419 | 395120 | 800 | 15.242 | 4.7624 | 8.2624 | 15.8004 | 5.1687 | 3.7148 | 8.2624 | 3.4214 | 6.4802 | N/A
HAVERTHWAITE | 11 | ULVERSTON | ULVERSTON | HARKER | 334234 | 483827 | 630 | 12.0031 | 4.4134 | 6.9134 | 13.0026 | 13.0026 | 13.0026 | 6.9134 | 13.0026 | 6.7952 | Offer signed, returned on 11/04/23
HAWK GREEN | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395915 | 387138 | 630 | 12.0031 | 11.2345 | 15.7345 | 30.5328 | 16.9282 | 12.1666 | 15.7345 | 12.0132 | 15.4515 | Offer signed, returned on 18/04/23
HAYDOCK | 11 | GOLBORNE | GOLBORNE | BOLD | 357489 | 397336 | 630 | 12.0031 | 11.9495 | 17.4495 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | N/A
HDA NO1 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301743 | 524532 | 400 | 7.621 | 13.1159 | 19.3359 | 6.7648 | 1.1138 | 0.80048 | 6.7648 | 0 | 0 | Offer signed, returned on 11/04/23
HDA NO2 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301429 | 525527 | 630 | 12.0031 | 13.1159 | 19.3359 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed, returned on 11/04/23
HEADY HILL | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 384370 | 410583 | 400 | 4.5726 | 5.2135 | 8.7135 | 24.7522 | 10.4582 | 7.6306 | 8.7135 | 7.0425 | 7.7035 | Data submitted, clock started 02/03/2023
HEAP BRIDGE | 6.6 | BURY | BURY | KEARSLEY | 382793 | 410428 | 400 | 4.5726 | 7.85 | 7.85 | 5.4729 | 1.9575 | 1.4344 | 5.4729 | 1.4344 | 2.695 | Offer signed, returned on 18/04/23
HEASANDFORD | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385349 | 433821 | 400 | 4.5726 | 9.4144 | 18.6244 | 29.9937 | 8.9682 | 6.5434 | 18.6244 | 0 | 0 | Data submitted, clock started 02/03/2023
HEATON MOOR | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 387623 | 391345 | 630 | 7.2019 | 5.8922 | 15.8922 | 31.1274 | 9.7172 | 7.0899 | 15.8922 | 7.1221 | 0 | Offer signed, returned on 18/04/23
HEATON NORRIS | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 388860 | 391967 | 400 | 4.5726 | 0.86379 | 7.8638 | 29.256 | 4.8963 | 3.5725 | 7.8638 | 3.0681 | 0 | Offer signed, returned on 18/04/23
HELWITH BRIDGE | 11 | PADIHAM | PADIHAM | PADIHAM | 381025 | 469428 | 630 | 12.0031 | 0.80386 | 8.8039 | 13.2972 | 13.2972 | 13.2972 | 8.8039 | 13.2972 | 8.3367 | Data Submitted, clock start due 27/05/23
HENSINGHAM | 11 | EGREMONT | EGREMONT | HARKER | 298465 | 517239 | 630 | 12.0031 | 12.1749 | 16.3119 | 25.8852 | 12.6103 | 9.0632 | 16.3119 | 9.101 | 17.1039 | Offer signed, returned on 11/04/23
HEYROD | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397310 | 399981 | 600 | 6.8589 | 9.6561 | 14.2931 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | N/A
HEYSIDE | 6.6 | ROYTON | ROYTON | WHITEGATE | 393433 | 407129 | 400 | 4.5726 | 11.4887 | 16.1257 | 0 | 0 | 0 | 0 | 0 | 0 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
HEYWOOD | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 385429 | 410369 | 630 | 7.2019 | 1.2504 | 2.3816 | 18.1269 | 2.9399 | 2.1451 | 2.3816 | 1.2885 | 0 | Data submitted, clock started 02/03/2023
HIGHER MILL | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385731 | 388090 | 400 | 4.5726 | 6.7425 | 14.2425 | 4.38 | 1.6977 | 1.4038 | 4.38 | 1.4344 | 5.768 | Offer now with ENW, due to be signed 16/08/2023
HIGHER WALTON | 11 | LEYLAND | LEYLAND | PENWORTHAM | 358020 | 427270 | 400 | 7.621 | 6.5422 | 11.1792 | 21.3152 | 5.3607 | 3.8529 | 11.1792 | 3.7037 | 4.126 | Offer signed, return on 14/03/23
HILL TOP T11 & T12 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373466 | 403748 | 400 | 7.621 | 5.5306 | 9.6706 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed, returned on 18/04/23
HILL TOP T13 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373476 | 403758 | 400 | 7.621 | 0.39996 | 0.39996 | 7 | 1.9575 | 1.4344 | 0.39996 | 1.4344 | 0.95096 | Offer signed, returned on 18/04/23
HINDLEY GREEN | 11 | ATHERTON | ATHERTON | KEARSLEY | 363389 | 403254 | 630 | 12.0031 | 7.3693 | 14.1893 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 0 | Offer signed, returned on 18/04/23
HOLLINWOOD | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 390287 | 402592 | 630 | 7.2019 | 13.4533 | 18.0903 | 26.6633 | 7.0967 | 5.1779 | 18.0903 | 1.3649 | 0 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
HOLME RD | 11 | RIBBLE | RIBBLE | PENWORTHAM | 352311 | 429141 | 400 | 7.621 | 6.954 | 11.091 | 11.2179 | 1.9575 | 1.4344 | 11.091 | 1.4344 | 11.2179 | Offer signed, return on 14/03/23
HOLT ST | 11 | BURY | BURY | KEARSLEY | 378620 | 416362 | 630 | 12.0031 | 3.9538 | 7.4538 | 11.2179 | 1.9575 | 1.4344 | 7.4538 | 1.4344 | 6.5258 | Offer signed, returned on 18/04/23
HURST | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 394658 | 400360 | 630 | 7.2019 | 6.1574 | 9.6574 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | N/A
HUTTON END | 11 | PENRITH & SHAP | PENRITH | HUTTON | 345810 | 538827 | 630 | 12.0031 | 6.0146 | 15.6546 | 21.6275 | 21.6275 | 16.6571 | 15.6546 | 17.2503 | 13.3736 | Awaiting payment for Hutton schemes
HYDE | 6.6 | HYDE | HYDE | STALYBRIDGE | 395215 | 395126 | 630 | 7.2019 | 6.8063 | 11.4433 | 31.4548 | 7.5812 | 5.5554 | 11.4433 | 5.4751 | 11.4433 | N/A
HYNDBURN RD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 375688 | 428877 | 800 | 9.1452 | 5.4125 | 17.7125 | 29.3612 | 13.6039 | 9.9258 | 17.7125 | 7.0436 | 17.6125 | Data Submitted, clock start due 27/05/23
INDIA ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369485 | 421865 | 400 | 4.5726 | 2.1176 | 17.3442 | 30.2557 | 5.5624 | 4.0761 | 17.3442 | 0 | 0 | Data submitted, clock started 02/03/2023
INGLETON | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 368913 | 472337 | 630 | 12.0031 | 1.7421 | 9.7421 | 12.6981 | 12.6981 | 12.6981 | 9.7421 | 0 | 0 | Awaiting payment for Hutton schemes
IRLAM | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 371680 | 393360 | 1250 | 14.2894 | 2.5089 | 6.6489 | 11.2179 | 1.9575 | 1.4344 | 6.6489 | 1.4344 | 4.4053 | N/A
JAMES ST | 11 | CARLISLE | CARLISLE | HARKER | 340034 | 555418 | 630 | 12.0031 | 7.4366 | 11.5736 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed, returned on 11/04/23
KAY ST | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373863 | 427594 | 630 | 7.2019 | 13.4855 | 17.6225 | 29.8132 | 13.7231 | 10.0127 | 17.6225 | 7.0436 | 16.5205 | Data Submitted, clock start due 27/05/23
KENDAL | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351915 | 491858 | 400 | 7.621 | 3.8934 | 8.0334 | 28.0218 | 9.4919 | 6.822 | 8.0334 | 0 | 0 | Awaiting payment for Hutton schemes
KESWICK | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 327022 | 523784 | 400 | 7.621 | 2.748 | 5.248 | 7 | 1.9575 | 1.4344 | 5.248 | 0 | 0 | Offer signed, returned on 11/04/23
KINGSWAY | 11 | BELFIELD | BELFIELD | ROCHDALE | 391636 | 411724 | 630 | 12.0031 | 20.8093 | 33.1273 | 45.8137 | 8.187 | 5.8842 | 33.1273 | 1.6009 | 0 | Data submitted, clock started 02/03/2023
KINKRY HILL | 11 | - | - | HARKER | 350800 | 575111 | 800 | 15.242 | 0.81619 | 2.3162 | 3.1954 | 3.1954 | 3.1954 | 2.3162 | 3.1954 | 2.3112 | Offer signed, returned on 11/04/23
KIRKBY LONSDALE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 359833 | 478813 | 400 | 7.621 | 2.2275 | 6.2275 | 13.7662 | 13.7662 | 13.7662 | 6.2275 | 0 | 0 | Awaiting payment for Hutton schemes
KIRKBY MOOR | 11 | ULVERSTON | ULVERSTON | HARKER | 326099 | 483011 | 1250 | 23.8157 | 2.2403 | 5.7403 | 3.4566 | 3.4566 | 3.4566 | 3.4566 | 2.8987 | 2.8987 | Offer signed, returned on 11/04/23
KIRKBY STEPHEN | 11 | PENRITH & SHAP | PENRITH | HUTTON | 376579 | 509136 | 800 | 15.242 | 8.1653 | 10.6653 | 19.5904 | 19.5904 | 19.5904 | 10.6653 | 19.5904 | 10.2783 | Awaiting payment for Hutton schemes
KIRKBY THORE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 364439 | 526672 | 630 | 12.0031 | 4.0843 | 15.3343 | 29.4281 | 25.768 | 18.52 | 15.3343 | 18.6543 | 13.2545 | Awaiting payment for Hutton schemes
KIRKHALL LANE | 11 | ATHERTON | ATHERTON | KEARSLEY | 365510 | 401069 | 400 | 7.621 | 6.1613 | 8.5113 | 19.9589 | 11.5928 | 8.332 | 8.5113 | 8.0695 | 0 | Offer signed, returned on 18/04/23
KITT GREEN | 6.6 | ORRELL | ORRELL | KIRKBY | 354934 | 405497 | 400 | 4.5726 | 4.6455 | 11.9197 | 31.9515 | 12.7581 | 9.3087 | 11.9197 | 9.0797 | 10.8837 | Data submitted for next PP. Awaiting clock start date
KNOTT MILL | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383136 | 397725 | 800 | 9.1452 | 4.3356 | 8.9726 | 31.367 | 6.8508 | 4.9985 | 8.9726 | 4.9077 | 0 | Offer now with ENW, due to be signed 16/08/2023
LAMBERHEAD | 6.6 | ORRELL | ORRELL | KIRKBY | 355516 | 404030 | 630 | 7.2019 | 10.6151 | 15.2551 | 24.478 | 9.9309 | 7.2459 | 15.2551 | 7.0795 | 15.6051 | Data submitted for next PP. Awaiting clock start date
LANCASTER | 11 | LANCASTER | LANCASTER | HEYSHAM | 348644 | 463628 | 630 | 12.0031 | 3.4477 | 7.5847 | 20.6623 | 3.4019 | 2.445 | 7.5847 | 1.5151 | 5.0572 | Data submitted, clock start due 02/03/2023
LANGLEY | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 386421 | 406330 | 400 | 7.621 | 8.677 | 13.314 | 33.1798 | 9.2058 | 6.7459 | 13.314 | 1.3649 | 0 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
LANGROYD RD | 6.6 | NELSON | NELSON | PADIHAM | 389077 | 440584 | 400 | 4.5726 | 9.2209 | 15.1298 | 0 | 0 | 0 | 0 | 0 | 0 | Data Submitted, clock start due 27/05/23
LEIGH | 11 | ATHERTON | ATHERTON | KEARSLEY | 365863 | 399907 | 800 | 15.242 | 2.7159 | 10.7159 | 19.6186 | 19.6186 | 19.6186 | 10.7159 | 19.6186 | 0 | Offer signed, returned on 18/04/23
LEVENSHULME | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 387494 | 394155 | 400 | 4.5726 | 4.1719 | 7.6719 | 25.4427 | 14.0146 | 10.2254 | 7.6719 | 10.1941 | 6.1719 | Offer signed, returned on 18/04/23
LEYLAND NATIONAL | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301973 | 525948 | 400 | 7.621 | 13.8269 | 21.612 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | Offer signed, returned on 11/04/23
LITTLE HULTON | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372024 | 403826 | 630 | 12.0031 | 2.4046 | 6.4546 | 7 | 1.9575 | 1.4344 | 6.4546 | 1.4344 | 4.4466 | Offer signed, returned on 18/04/23
LITTLE SALKELD | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356221 | 537513 | 400 | 7.621 | 7.3718 | 9.531 | 16.5605 | 16.5605 | 16.5605 | 9.531 | 16.5605 | 4.0762 | Awaiting payment for Hutton schemes
LITTLEBOROUGH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 393221 | 416124 | 400 | 4.5726 | 3.2446 | 6.7446 | 25.0991 | 9.8386 | 7.1785 | 6.7446 | 6.9929 | 0 | Data submitted, clock started 02/03/2023
LONGFORD BRIDGE | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380056 | 395083 | 800 | 9.1452 | 9.5998 | 14.2368 | 31.2344 | 7.7139 | 5.6283 | 14.2368 | 5.7031 | 10.4658 | Offer now with ENW, due to be signed 16/08/2023
LONGRIDGE | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 360581 | 437001 | 400 | 4.5726 | 2.1449 | 2.1449 | 11.2179 | 1.9575 | 1.4344 | 2.1449 | 1.4344 | 0 | Offer signed, return on 14/03/23
LONGSIGHT | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385535 | 396037 | 400 | 4.5726 | 6.5232 | 10.6602 | 27.2475 | 5.3608 | 3.9114 | 10.6602 | 2.8907 | 9.1882 | Offer signed, returned on 18/04/23
LOSTOCK | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365293 | 409079 | 800 | 15.242 | 7.2007 | 13.2007 | 34.8385 | 5.7359 | 4.1225 | 13.2007 | 0.088852 | 0 | Offer signed, returned on 18/04/23
LOWER DARWEN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369695 | 424981 | 800 | 9.1452 | 2.1176 | 16.8177 | 30.8138 | 5.5624 | 4.0761 | 16.8177 | 0 | 0 | Data submitted, clock started 02/03/2023
LYONS RD | 6.6 | BARTON | BARTON | CARRINGTON | 378253 | 397241 | 400 | 4.5726 | 10.8536 | 15.4906 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.6576 | N/A
MANCHESTER UNIVERSITY | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384762 | 396769 | 800 | 9.1452 | 0.41262 | 4.5496 | 30.0909 | 10.5199 | 7.6756 | 4.5496 | 7.4513 | 1.5496 | Offer signed, returned on 18/04/23
MARPLE | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395671 | 388643 | 630 | 12.0031 | 0.050606 | 0.050606 | 7.1061 | 7.1061 | 7.1061 | 0.050606 | 7.1061 | 0 | Offer signed, returned on 18/04/23
MARTON | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 333341 | 433485 | 400 | 4.5726 | 11.2324 | 15.8324 | 24.6386 | 8.6711 | 6.3267 | 15.8324 | 6.5522 | 14.5624 | Offer signed, return on 14/03/23
MARYPORT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 303716 | 535313 | 630 | 12.0031 | 8.9793 | 17.7029 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed, returned on 11/04/23
MELLING | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 360144 | 471643 | 630 | 12.0031 | 1.451 | 3.451 | 7.1573 | 7.1573 | 7.1573 | 3.451 | 0 | 0 | Awaiting payment for Hutton schemes
MERESIDE | 6.6 | PEEL | PEEL | PENWORTHAM | 334431 | 434843 | 630 | 7.2019 | 2.1727 | 2.1727 | 2.4151 | 2.4151 | 2.4151 | 2.1727 | 0 | 0 | Offer signed, return on 14/03/23
MIDDLETON JUNCTION | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 388606 | 405292 | 630 | 12.0031 | 5.5245 | 10.0245 | 28.4787 | 4.6888 | 3.3699 | 10.0245 | 1.3649 | 0 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
MIDWAY | 11 | EGREMONT | EGREMONT | HARKER | 304525 | 501993 | 630 | 12.0031 | 8.9798 | 11.7796 | 18.7067 | 18.7067 | 18.0985 | 11.7796 | 18.0835 | 11.4916 | Offer signed, returned on 11/04/23
MILNROW | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 392351 | 413056 | 400 | 4.5726 | 10.8122 | 15.4522 | 30.1883 | 10.5773 | 7.7175 | 15.4522 | 7.4802 | 14.0754 | Data submitted, clock started 02/03/2023
MINTSFEET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351827 | 494315 | 400 | 7.621 | 1.7322 | 7.7322 | 17.1689 | 2.8267 | 2.0316 | 7.7322 | 0 | 0 | Awaiting payment for Hutton schemes
MONSALL | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386332 | 401003 | 630 | 7.2019 | 11.8274 | 15.3274 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | N/A
MONTON | 6.6 | BARTON | BARTON | CARRINGTON | 376321 | 399494 | 400 | 4.5726 | 3.7149 | 7.2149 | 11.2179 | 1.9575 | 1.4344 | 7.2149 | 1.4344 | 5.0297 | N/A
MOORSIDE | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349331 | 435746 | 630 | 7.2019 | 3.7944 | 7.2944 | 11.2179 | 1.9575 | 1.4344 | 7.2944 | 1.4344 | 8.9507 | Offer signed, return on 14/03/23
MORTON PARK | 11 | CARLISLE | CARLISLE | HARKER | 337826 | 553939 | 1250 | 23.8157 | 8.3041 | 12.1041 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | Offer signed, returned on 11/04/23
MOSLEY RD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 379058 | 396289 | 630 | 7.2019 | 3.4902 | 6.9902 | 23.7167 | 8.7856 | 6.4102 | 6.9902 | 5.8695 | 0 | Offer now with ENW, due to be signed 16/08/2023
MOSS LANE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 380858 | 405856 | 400 | 7.621 | 0.98997 | 5.127 | 7 | 1.9575 | 1.4344 | 5.127 | 1.4344 | 3.7702 | Offer signed, returned on 18/04/23
MOSS NOOK PRIMARY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384084 | 385010 | 800 | 15.242 | 17.594 | 24.1413 | 4.38 | 1.6977 | 1.4038 | 4.38 | 1.4344 | 5.768 | Offer now with ENW, due to be signed 16/08/2023
MOSS SIDE (Leyland) | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352170 | 422970 | 400 | 7.621 | 3.3845 | 6.6985 | 27.9116 | 13.2189 | 9.5007 | 6.6985 | 9.1199 | 4.5253 | Offer signed, return on 14/03/23
MOSS SIDE (Longsight) | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384007 | 395893 | 400 | 4.5726 | 0 | 5.9344 | 31.5971 | 10.0767 | 7.3522 | 5.9344 | 7.5673 | 1.6732 | Offer signed, returned on 18/04/23
MOSSLEY | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397437 | 401979 | 400 | 7.621 | 9.6226 | 14.2596 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | N/A
MOUNT ST | 6.6 | BARTON | BARTON | CARRINGTON | 376250 | 397574 | 400 | 4.5726 | 9.9785 | 14.6154 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 8.7054 | N/A
MUSGRAVE RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 370045 | 409863 | 800 | 9.1452 | 8.69 | 14.31 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed, returned on 18/04/23
NELSON | 6.6 | NELSON | NELSON | PADIHAM | 386020 | 438507 | 400 | 4.5726 | 6.5634 | 10.7034 | 0 | 0 | 0 | 0 | 0 | 0 | Data Submitted, clock start due 27/05/23
NEW MOSTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388333 | 402657 | 630 | 7.2019 | 10.6779 | 15.3149 | 31.0839 | 9.2058 | 6.7459 | 15.3149 | 1.3649 | 0 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
NEWBIGGIN ON LUNE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 369770 | 505803 | 800 | 15.242 | 0.5408 | 2.0408 | 3.8322 | 3.8322 | 3.8322 | 2.0408 | 3.8322 | 2.0546 | Awaiting payment for Hutton schemes
NEWBY | 11 | PENRITH & SHAP | PENRITH | HUTTON | 360520 | 521151 | 400 | 7.621 | 0.60107 | 7.6011 | 15.0523 | 15.0523 | 15.0523 | 7.6011 | 15.0523 | 7.0631 | Awaiting payment for Hutton schemes
NEWTON | 11 | HYDE | HYDE | STALYBRIDGE | 396385 | 396464 | 400 | 7.621 | 9.8163 | 15.5743 | 8.0566 | 7.5812 | 5.5554 | 8.0566 | 1.511 | 1.511 | N/A
NEWTON HEATH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388030 | 400511 | 400 | 4.5726 | 0 | 0 | 12.0025 | 9.2058 | 6.7459 | 0 | 1.3649 | 0 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
NEWTON LE WILLOWS | 11 | GOLBORNE | GOLBORNE | BOLD | 357891 | 395944 | 630 | 12.0031 | 8.8891 | 13.0261 | 28.3704 | 11.4509 | 8.23 | 13.0261 | 0 | 0 | N/A
NEWTONGATE T11 & T12 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 5.9733 | 9.9733 | 31.4059 | 5.259 | 3.7797 | 9.9733 | 3.841 | 8.6565 | Awaiting payment for Hutton schemes
NEWTONGATE T13 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 6.6922 | 11.4422 | 16.5236 | 16.5236 | 16.227 | 11.4422 | 14.4183 | 10.2752 | Awaiting payment for Hutton schemes
NORBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331831 | 441463 | 400 | 4.5726 | 17.3747 | 22.8902 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed, return on 14/03/23
NORBURY | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392447 | 385492 | 400 | 7.621 | 11.8458 | 16.4828 | 6.3074 | 1.0385 | 0.74636 | 6.3074 | 0.56343 | 4.7615 | Offer signed, returned on 18/04/23
NORTHENDEN | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382555 | 390327 | 400 | 4.5726 | 7.5086 | 11.0086 | 11.2179 | 1.9575 | 1.4344 | 11.0086 | 1.4344 | 9.31 | Offer now with ENW, due to be signed 16/08/2023
NWGB PARTINGTON | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 372569 | 392079 | 400 | 4.5726 | 4.7828 | 9.7228 | 11.2179 | 1.9575 | 1.4344 | 9.7228 | 1.4344 | 10.0382 | N/A
OFFERTON | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 391010 | 389489 | 400 | 4.5726 | 8.5727 | 18.8272 | 30.5974 | 12.5777 | 9.1771 | 18.8272 | 9.1327 | 0 | Offer signed, returned on 18/04/23
OPENSHAW | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 388606 | 397346 | 630 | 7.2019 | 3.139 | 6.639 | 25.7553 | 5.2662 | 3.859 | 6.639 | 1.4344 | 5.886 | N/A
ORMSKIRK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 341294 | 408158 | 800 | 15.242 | 8.707 | 13.344 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.4513 | N/A
PADIHAM | 11 | PADIHAM | PADIHAM | PADIHAM | 378428 | 433238 | 400 | 7.621 | 17.1555 | 24.1555 | 5.782 | 0.95196 | 0.68419 | 5.782 | 0.84345 | 7.1279 | Data Submitted, clock start due 27/05/23
PEEL ST | 11 | PADIHAM | PADIHAM | PADIHAM | 374463 | 441514 | 630 | 12.0031 | 0.6174 | 10.4174 | 19.6031 | 19.6031 | 19.6031 | 10.4174 | 19.6031 | 8.983 | Data Submitted, clock start due 27/05/23
PENDLETON | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381161 | 398842 | 400 | 4.5726 | 0 | 13.5834 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed, returned on 18/04/23
PETTERIL BANK | 11 | CARLISLE | CARLISLE | HARKER | 341768 | 553686 | 400 | 7.621 | 8.222 | 12.359 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed, returned on 11/04/23
PHILLIPS LANE | 6.6 | NELSON | NELSON | PADIHAM | 387571 | 439522 | 800 | 9.1452 | 2.2154 | 11.2154 | 0 | 0 | 0 | 0 | 0 | 0 | Data Submitted, clock start due 27/05/23
PICCADILLY | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 384427 | 398261 | 400 | 4.5726 | 11.6816 | 18.1725 | 29.5281 | 8.4744 | 6.1832 | 18.1725 | 6.0414 | 15.0117 | Offer now with ENW, due to be signed 16/08/2023
PIMBO | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 349148 | 404549 | 400 | 7.621 | 9.9112 | 24.9112 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.4513 | N/A
PIRELLI | 11 | CARLISLE | CARLISLE | HARKER | 339059 | 553548 | 400 | 7.621 | 7.7571 | 11.5571 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed, returned on 11/04/23
PORTWOOD | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 389826 | 390619 | 400 | 4.5726 | 2.97 | 7.607 | 31.2648 | 9.3471 | 6.8199 | 7.607 | 6.7371 | 0 | Offer signed, returned on 18/04/23
POULTON | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 335679 | 439130 | 800 | 9.1452 | 9.3033 | 11.2833 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 6.9765 | Offer signed, return on 14/03/23
POYNTON | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392096 | 383493 | 630 | 12.0031 | 8.0179 | 11.5179 | 23.6228 | 13.0943 | 9.4112 | 11.5179 | 9.4181 | 10.8112 | Offer signed, returned on 18/04/23
PREESALL | 11 | THORNTON | THORNTON | STANAH | 336965 | 446547 | 800 | 15.242 | 11.7837 | 16.2837 | 30.5675 | 13.1145 | 9.6102 | 16.2837 | 9.0987 | 15.8281 | N/A
PRESTON EAST | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356777 | 432926 | 630 | 7.2019 | 2.1449 | 2.1449 | 2.6918 | 0.43658 | 0.31854 | 2.1449 | 1.4344 | 0 | Offer signed, return on 14/03/23
PRESTON OLD RD | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332562 | 434929 | 800 | 9.1452 | 12.501 | 17.138 | 30.2268 | 11.9153 | 8.6937 | 17.138 | 8.77 | 17.138 | Offer signed, return on 14/03/23
PRESTWICH | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 381392 | 404001 | 400 | 4.5726 | 5.1776 | 9.8146 | 32.1779 | 7.9785 | 5.8213 | 9.8146 | 5.8553 | 6.3816 | Offer signed, returned on 18/04/23
PRINGLE ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369088 | 427387 | 400 | 4.5726 | 9.6913 | 17.2513 | 30.2531 | 12.2755 | 8.9566 | 17.2513 | 8.8549 | 17.2513 | Offer signed, return on 14/03/23
PRINNY HILL | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378328 | 423395 | 630 | 7.2019 | 9.2872 | 14.3872 | 24.7332 | 13.6288 | 9.9439 | 14.3872 | 9.5083 | 14.3872 | Data Submitted, clock start due 27/05/23
QUEENS PARK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 385893 | 400645 | 400 | 4.5726 | 9.9118 | 11.9321 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | N/A
RADCLIFFE | 11 | - | - | KEARSLEY | 377524 | 406160 | 400 | 7.621 | 11.2433 | 11.6433 | 43.9949 | 12.2676 | 8.817 | 11.6433 | 8.7443 | 5.7413 | Offer signed, returned on 18/04/23
RANDAL ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 368092 | 428515 | 630 | 7.2019 | 5.8129 | 18.5129 | 34.9192 | 12.7658 | 9.3143 | 18.5129 | 8.8192 | 17.3639 | Offer signed, return on 14/03/23
RAWTENSTALL RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 379395 | 422143 | 630 | 7.2019 | 10.5965 | 15.2335 | 30.169 | 16.0737 | 11.7278 | 15.2335 | 11.7382 | 14.2835 | Data Submitted, clock start due 27/05/23
REDDISH VALE | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 390147 | 393309 | 800 | 9.1452 | 6.5128 | 15.5128 | 30.3545 | 9.8079 | 7.1561 | 15.5128 | 7.0914 | 0 | Offer signed, returned on 18/04/23
RIBBLESDALE T13 & RIBBLESDALE T14 | 11 | PADIHAM | PADIHAM | PADIHAM | 374759 | 443587 | 800 | 15.242 | 1.8038 | 4.5538 | 22.1282 | 15.8991 | 11.427 | 4.5538 | 11.8923 | 1.683 | Data Submitted, clock start due 27/05/23
RIBBLETON | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356730 | 431506 | 630 | 7.2019 | 2.1449 | 2.1449 | 11.2179 | 1.9575 | 1.4344 | 2.1449 | 1.4344 | 0 | Offer signed, return on 14/03/23
RINGLEY | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376120 | 405531 | 630 | 12.0031 | 14.8188 | 15.153 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed, returned on 18/04/23
RISLEY | 11 | - | - | BOLD | 365181 | 392989 | 400 | 7.621 | 0 | 9.3059 | 9.1607 | 1.5082 | 1.084 | 9.1607 | 1.2626 | 4.1747 | N/A
ROBERT HALL ST | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381359 | 397718 | 400 | 4.5726 | 0 | 14.0825 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed, returned on 18/04/23
ROCHDALE CENTRAL | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 389111 | 413393 | 630 | 7.2019 | 17.5367 | 30.5367 | 1.1594 | 0.18803 | 0.13719 | 1.1594 | 0.31848 | 2.6914 | Data submitted, clock started 02/03/2023
ROMAN RD | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369058 | 426505 | 630 | 7.2019 | 2.1176 | 15.1705 | 30.3511 | 5.5624 | 4.0761 | 15.1705 | 0 | 0 | Data submitted, clock started 02/03/2023
ROMILEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393626 | 390716 | 400 | 7.621 | 2.7442 | 6.2442 | 24.0007 | 10.9941 | 7.9016 | 6.2442 | 7.5834 | 0 | Offer signed, returned on 18/04/23
ROSSALL | 6.6 | THORNTON | THORNTON | STANAH | 331916 | 445505 | 400 | 4.5726 | 0 | 3.109 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
ROYTON | 6.6 | ROYTON | ROYTON | WHITEGATE | 392426 | 407533 | 800 | 9.1452 | 11.3967 | 16.0337 | 0 | 0 | 0 | 0 | 0 | 0 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
SALE | 6.6 | SALE | SALE | CARRINGTON | 378952 | 392177 | 630 | 7.2019 | 11.0305 | 15.6705 | 31.0489 | 8.5345 | 6.227 | 15.6705 | 6.5677 | 14.7385 | N/A
SALE MOOR | 6.6 | SALE | SALE | CARRINGTON | 379671 | 391133 | 400 | 4.5726 | 1.5401 | 1.5401 | 12.01 | 12.01 | 12.01 | 1.5401 | 12.01 | 1.3941 | N/A
SALFORD QUAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 380334 | 397555 | 800 | 9.1452 | 0 | 16.67 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed, returned on 18/04/23
SANDGATE | 11 | BARROW & SANDGATE | BARROW | HARKER | 321492 | 468870 | 630 | 12.0031 | 10.3066 | 14.8066 | 30.2683 | 9.8093 | 7.0501 | 14.8066 | 7.2924 | 14.3266 | Offer signed, returned on 11/04/23
SCARISBRICK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 338069 | 412086 | 400 | 7.621 | 2.1832 | 3.6832 | 6.4667 | 1.9575 | 1.4344 | 3.6832 | 1.4344 | 3.6656 | N/A
SEBERGHAM | 11 | CARLISLE | CARLISLE | HARKER | 335344 | 542653 | 630 | 12.0031 | 0.24938 | 1.2494 | 1.9438 | 1.9438 | 1.4344 | 1.2494 | 1.4344 | 1.1732 | Offer signed, returned on 11/04/23
SEDBERGH | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 365151 | 491747 | 400 | 7.621 | 2.9652 | 12.8444 | 19.5532 | 19.5532 | 19.3081 | 12.8444 | 0 | 0 | Awaiting payment for Hutton schemes
SELSMIRE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 361018 | 507505 | 630 | 12.0031 | 1.1693 | 1.1693 | 4.9054 | 4.9054 | 4.9054 | 1.1693 | 4.9054 | 1.1883 | Awaiting payment for Hutton schemes
SETTLE | 11 | PADIHAM | PADIHAM | PADIHAM | 381588 | 463721 | 630 | 12.0031 | 0.39881 | 7.8988 | 13.3716 | 13.3716 | 13.3716 | 7.8988 | 13.3716 | 7.6618 | Data Submitted, clock start due 27/05/23
SEVEN STARS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352653 | 421636 | 800 | 15.242 | 1.0585 | 7.4085 | 32.0548 | 26.5912 | 19.1116 | 7.4085 | 18.9995 | 5.2353 | Offer signed, return on 14/03/23
SHANNON ST SOUTH | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330806 | 435291 | 630 | 7.2019 | 4.417 | 9.917 | 32.1479 | 11.0898 | 8.0914 | 9.917 | 8.0106 | 5.397 | Offer signed, return on 14/03/23
SHAP | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356910 | 513357 | 400 | 7.621 | 4.3518 | 7.1518 | 12.2325 | 12.2325 | 12.2325 | 7.1518 | 12.2325 | 7.0318 | Awaiting payment for Hutton schemes
SHAW | 6.6 | ROYTON | ROYTON | WHITEGATE | 394298 | 409450 | 800 | 9.1452 | 9.7528 | 14.3898 | 0 | 0 | 0 | 0 | 0 | 0 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
Siddick | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300289 | 530805 | 630 | 12.0031 | 17.322 | 23.9128 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | Offer signed, returned on 11/04/23
SILLOTH | 11 | CARLISLE | CARLISLE | HARKER | 311307 | 553464 | 400 | 7.621 | 19.1709 | 41.5095 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed, returned on 11/04/23
SKELMERSDALE | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347198 | 407434 | 630 | 12.0031 | 5.8808 | 10.5178 | 11.2179 | 1.9575 | 1.4344 | 10.5178 | 1.3976 | 7.809 | N/A
SKELTON C | 11 | PENRITH & SHAP | PENRITH | HUTTON | 342672 | 538337 | 630 | 12.0031 | 6.0146 | 15.6546 | 30.438 | 24.0672 | 17.2976 | 15.6546 | 17.7881 | 13.3736 | Awaiting payment for Hutton schemes
SLIPWAY | 11 | EGREMONT | EGREMONT | HARKER | 297180 | 518183 | 400 | 7.621 | 6.0159 | 8.0159 | 16.7034 | 16.7034 | 12.3484 | 8.0159 | 12.7115 | 7.3459 | Offer signed, returned on 11/04/23
SNIPE | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 391844 | 398322 | 800 | 9.1452 | 9.397 | 14.034 | 30.1795 | 5.2662 | 3.859 | 14.034 | 1.4344 | 11.2179 | N/A
S.E. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392001 | 372504 | 630 | 12.0031 | 6.9671 | 6.9671 | 11.2179 | 1.9575 | 1.4344 | 6.9671 | 1.4344 | 0 | N/A
SOUTH PARK | 11 | LYTHAM | LYTHAM | PENWORTHAM | 336410 | 427512 | 400 | 7.621 | 0 | 0 | 19.8677 | 11.6116 | 8.3455 | 0 | 0 | 0 | Offer signed, return on 14/03/23
S.W. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 390968 | 373004 | 400 | 7.621 | 4.5336 | 6.9671 | 11.2179 | 1.9575 | 1.4344 | 6.9671 | 1.4344 | 0 | N/A
SPA RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 371065 | 409109 | 400 | 4.5726 | 7.0665 | 7.0665 | 11.2179 | 1.9575 | 1.4344 | 7.0665 | 1.4344 | 5.2215 | Offer signed, returned on 18/04/23
SPADEADAM 132/11KV | 11 | - | - | HARKER | 361282 | 570359 | 1250 | 23.8157 | 25.6935 | 32.6935 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offer signed, returned on 11/04/23
SPOTLAND | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 387882 | 414309 | 630 | 7.2019 | 6.9856 | 10.4856 | 23.6188 | 13.4182 | 9.7903 | 10.4856 | 4.1691 | 9.6296 | Data submitted, clock started 02/03/2023
SPRING COTTAGE | 6.6 | NELSON | NELSON | PADIHAM | 385446 | 437481 | 400 | 4.5726 | 5.7636 | 19.5116 | 0 | 0 | 0 | 0 | 0 | 0 | Data Submitted, clock start due 27/05/23
SPRING GARDEN ST 11kV | 11 | LANCASTER | LANCASTER | HEYSHAM | 347661 | 461494 | 800 | 15.242 | 15.6955 | 19.187 | 26.8051 | 4.6774 | 3.4275 | 19.187 | 1.5151 | 5.0572 | Data submitted, clock start due 02/03/2023
SPRING GARDEN ST 6.6KV | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 347651 | 461484 | 800 | 9.1452 | 12.6689 | 16.8059 | 26.8051 | 4.6774 | 3.4275 | 16.8059 | 1.5151 | 5.0572 | Data submitted, clock start due 02/03/2023
SQUIRES GATE | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332037 | 432063 | 400 | 4.5726 | 6.6055 | 11.2055 | 19.424 | 3.1503 | 2.2985 | 11.2055 | 2.1114 | 6.2955 | Offer signed, return on 14/03/23
ST ANNES | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 331716 | 429849 | 630 | 7.2019 | 0 | 0 | 19.8677 | 9.884 | 7.2116 | 0 | 0 | 0 | Offer signed, return on 14/03/23
ST MARYS | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 392582 | 405316 | 630 | 7.2019 | 15.0845 | 19.7215 | 29.2752 | 10.4518 | 7.6259 | 19.7215 | 7.7148 | 4.6017 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
ST MARYS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 354932 | 429640 | 400 | 4.5726 | 7.1664 | 10.6664 | 11.2179 | 1.9575 | 1.4344 | 10.6664 | 1.4344 | 10.0664 | Offer signed, return on 14/03/23
ST THOMAS RD | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 332713 | 428643 | 400 | 4.5726 | 0 | 0 | 19.8677 | 13.0673 | 9.5343 | 0 | 0 | 0 | Offer signed, return on 14/03/23
STAINBURN | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 302535 | 529330 | 630 | 12.0031 | 8.2537 | 10.7537 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed, returned on 11/04/23
STANDISH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 356139 | 410059 | 630 | 12.0031 | 5.6962 | 7.8902 | 11.2756 | 5.3659 | 3.8565 | 7.8902 | 1.9914 | 1.9914 | Offer signed, return on 14/03/23
STRANGEWAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383780 | 399743 | 400 | 4.5726 | 0 | 15.2423 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed, returned on 18/04/23
STRAWBERRY BANK | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 376338 | 429396 | 630 | 7.2019 | 6.0718 | 10.2088 | 20.9842 | 3.7185 | 2.7131 | 10.2088 | 2.4384 | 6.5078 | Data Submitted, clock start due 27/05/23
STUART ST | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387190 | 398835 | 600 | 6.8589 | 8.6279 | 15.6279 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | N/A
STUBBINS | 11 | ROSSENDALE | ROSSENDALE | PADIHAM | 379112 | 418005 | 400 | 7.621 | 10.6665 | 27.6665 | 31.0443 | 5.1112 | 3.6735 | 27.6665 | 2.782 | 23.5098 | Data Submitted, clock start due 27/05/23
SWINTON | 11 | AGECROFT | AGECROFT | KEARSLEY | 378367 | 401718 | 800 | 15.242 | 13.6986 | 18.1986 | 30.2092 | 15.1433 | 10.8838 | 18.1986 | 10.853 | 18.1986 | Offer signed, returned on 18/04/23
TAME VALLEY | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 395148 | 398108 | 630 | 7.2019 | 8.836 | 13.473 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | N/A
TARDY GATE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 353958 | 426066 | 400 | 7.621 | 7.6344 | 11.7714 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.065 | Offer signed, return on 14/03/23
TARLETON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344741 | 422417 | 400 | 7.621 | 4.8326 | 7.8902 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | Offer signed, return on 14/03/23
THE HEIGHT | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 379792 | 400497 | 400 | 4.5726 | 5.0921 | 15.7921 | 29.77 | 10.1373 | 7.3964 | 15.7921 | 7.3789 | 14.5981 | Offer signed, returned on 18/04/23
THORNTON | 11 | BISPHAM | BISPHAM | PENWORTHAM | 334207 | 442111 | 630 | 12.0031 | 9.7998 | 12.9368 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 0.31765 | 2.6844 | Offer signed, return on 14/03/23
TOWNLEY ST | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 387242 | 405960 | 400 | 7.621 | 3.8675 | 20.1255 | 33.4932 | 9.1845 | 6.6011 | 20.1255 | 1.3649 | 0 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
TRAFFORD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380714 | 396551 | 630 | 7.2019 | 7.3565 | 14.3565 | 22.3705 | 7.7367 | 5.6449 | 14.3565 | 5.7122 | 14.3365 | Offer now with ENW, due to be signed 16/08/2023
TRAFFORD PARK NORTH | 6.6 | BARTON | BARTON | CARRINGTON | 378738 | 397694 | 630 | 7.2019 | 6.2399 | 11.4899 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | N/A
TRIMPELL | 11 | - | - | HEYSHAM | 341861 | 458979 | 630 | 12.0031 | 19.7099 | 19.7099 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Data submitted, clock start due 02/03/2023
TRINITY | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 382649 | 398230 | 630 | 7.2019 | 0 | 25.0525 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed, returned on 18/04/23
TULKETH | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352393 | 431036 | 400 | 4.5726 | 6.7871 | 10.9241 | 11.2179 | 1.9575 | 1.4344 | 10.9241 | 1.4344 | 8.4618 | Offer signed, return on 14/03/23
ULVERSTON | 11 | ULVERSTON | ULVERSTON | HARKER | 327495 | 477808 | 630 | 12.0031 | 5.0745 | 8.0745 | 16.3552 | 10.6016 | 7.6196 | 8.0745 | 7.6223 | 7.75 | Offer signed, returned on 11/04/23
UNION RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 372174 | 410598 | 630 | 7.2019 | 6.2262 | 10.8632 | 11.2179 | 1.9575 | 1.4344 | 10.8632 | 1.4344 | 9.7198 | Offer signed, returned on 18/04/23
UPHOLLAND | 11 | ORRELL | ORRELL | KIRKBY | 352531 | 404369 | 630 | 12.0031 | 3.6767 | 7.1767 | 22.0084 | 11.6572 | 8.3783 | 7.1767 | 8.1328 | 6.6945 | Data submitted for next PP. Awaiting clock start date
URMSTON | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 377117 | 395709 | 400 | 4.5726 | 10.5241 | 15.1611 | 28.9446 | 7.7241 | 5.6357 | 15.1611 | 5.7691 | 14.4783 | Offer now with ENW, due to be signed 16/08/2023
VICTORIA PARK | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385373 | 395948 | 630 | 7.2019 | 3.9899 | 10.4899 | 25.5112 | 8.2386 | 6.0111 | 10.4899 | 4.6312 | 4.9475 | Offer signed, returned on 18/04/23
WARBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331775 | 438420 | 630 | 7.2019 | 7.4371 | 10.9371 | 11.2179 | 1.9575 | 1.4344 | 10.9371 | 1.4344 | 10.9371 | Offer signed, return on 14/03/23
WARDLEWORTH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 390339 | 414050 | 630 | 7.2019 | 7.0193 | 11.6563 | 31.4551 | 7.9437 | 5.7959 | 11.6563 | 5.5739 | 0 | Data submitted, clock started 02/03/2023
WARTON | 6.6 | PEEL | PEEL | PENWORTHAM | 341290 | 428540 | 1250 | 14.2894 | 2.1727 | 2.1727 | 2.4151 | 2.4151 | 2.4151 | 2.1727 | 0 | 0 | Offer signed, return on 14/03/23
WATERHEAD | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 394942 | 405940 | 400 | 4.5726 | 14.6569 | 19.2939 | 29.365 | 12.6699 | 9.2443 | 19.2939 | 9.344 | 4.6017 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
WATERSWALLOWS | 11 | BUXTON | BUXTON | STALYBRIDGE | 407734 | 375459 | 630 | 12.0031 | 11.4832 | 17.3855 | 28.4979 | 11.171 | 8.0288 | 17.3855 | 1.3561 | 10.6051 | N/A
WEASTE | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 378751 | 398897 | 800 | 9.1452 | 0 | 9.7815 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | Offer signed, returned on 18/04/23
WERNETH | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391273 | 403453 | 630 | 7.2019 | 13.7613 | 18.3983 | 30.177 | 12.4321 | 9.0708 | 18.3983 | 8.8768 | 4.6017 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
WESLEY PLACE BACUP | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 386475 | 422130 | 400 | 4.5726 | 7.6763 | 12.3133 | 30.2639 | 14.2858 | 10.4233 | 12.3133 | 10.1945 | 7.7239 | Data Submitted, clock start due 27/05/23
WEST DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 383306 | 392514 | 630 | 7.2019 | 3.7903 | 10.7903 | 11.2179 | 1.9575 | 1.4344 | 10.7903 | 1.4344 | 8.6933 | Offer now with ENW, due to be signed 16/08/2023
WESTGATE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343077 | 463204 | 630 | 7.2019 | 3.5693 | 5.3824 | 18.3146 | 4.6774 | 3.4275 | 5.3824 | 1.5151 | 5.0572 | Data submitted, clock start due 02/03/2023
WESTHOUGHTON | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365831 | 407025 | 400 | 7.621 | 3.0946 | 7.7316 | 9.9189 | 1.6331 | 1.1737 | 7.7316 | 0.088852 | 0 | Offer signed, returned on 18/04/23
WESTLINTON | 11 | CARLISLE | CARLISLE | HARKER | 339551 | 564489 | 630 | 12.0031 | 8.9095 | 12.0458 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed, returned on 11/04/23
WHALLEY | 11 | PADIHAM | PADIHAM | PADIHAM | 373376 | 436176 | 630 | 12.0031 | 9.0359 | 13.6729 | 28.3048 | 8.1611 | 5.8656 | 13.6729 | 5.5392 | 11.0853 | Data Submitted, clock start due 27/05/23
WHALLEY RANGE | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382923 | 394645 | 630 | 7.2019 | 1.902 | 11.039 | 11.2179 | 1.9575 | 1.4344 | 11.039 | 1.4344 | 10.576 | Offer now with ENW, due to be signed 16/08/2023
WHASSET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 350648 | 481468 | 630 | 12.0031 | 2.7877 | 6.7877 | 23.0587 | 20.6764 | 14.8605 | 6.7877 | 0 | 0 | Awaiting payment for Hutton schemes
WHITTLE LE WOODS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 357874 | 421203 | 630 | 12.0031 | 5.9526 | 9.4526 | 23.9575 | 14.5691 | 10.4711 | 9.4526 | 10.3146 | 9.0214 | Offer signed, return on 14/03/23
WHITWORTH | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 388779 | 419157 | 630 | 7.2 | 4.6864 | 6.1864 | 10.5081 | 4.6773 | 3.4127 | 6.1864 | 3.1391 | 5.9064 | Data submitted, clock started 02/03/2023
WIGTON | 11 | CARLISLE | CARLISLE | HARKER | 325814 | 549933 | 400 | 7.621 | 0 | 2.4373 | 7 | 1.9575 | 1.4344 | 2.4373 | 1.4344 | 0.21045 | Offer signed, returned on 11/04/23
WILLOW HEY | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347779 | 406066 | 400 | 7.621 | 8.763 | 13.4 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.682 | N/A
WILLOWBANK | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391885 | 406064 | 630 | 7.2019 | 2.476 | 5.976 | 25.3471 | 12.4815 | 9.1068 | 5.976 | 9.2635 | 4.6017 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
WILLOWHOLME | 11 | CARLISLE | CARLISLE | HARKER | 338653 | 556688 | 630 | 12.0031 | 8.8304 | 12.9674 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed, returned on 11/04/23
WILMSLOW | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384710 | 381286 | 630 | 12.0031 | 5.1333 | 8.6333 | 4.38 | 1.6977 | 1.4038 | 4.38 | 1.4344 | 5.768 | Offer now with ENW, due to be signed 16/08/2023
WINDERMERE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 341657 | 498418 | 630 | 12.0031 | 9.5614 | 13.5614 | 30.4268 | 20.6687 | 14.855 | 13.5614 | 0 | 0 | Awaiting payment for Hutton schemes
WINIFRED RD | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 389971 | 388470 | 630 | 7.2019 | 5.6347 | 9.1347 | 18.0363 | 5.0272 | 3.668 | 9.1347 | 2.1791 | 7.5047 | Offer signed, returned on 18/04/23
WITHINGTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384841 | 392774 | 630 | 7.2019 | 3.0832 | 6.5832 | 11.2179 | 1.9575 | 1.4344 | 6.5832 | 1.4344 | 6.0832 | Offer now with ENW, due to be signed 16/08/2023
WITHYFOLD DRIVE | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392132 | 374352 | 400 | 7.621 | 6.9671 | 6.9671 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 0 | N/A
WOODBINE ST | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 390519 | 412388 | 800 | 9.1452 | 5.8536 | 9.3536 | 24.1055 | 14.5138 | 10.5896 | 9.3536 | 10.5673 | 8.8316 | Data submitted, clock started 02/03/2023
WOODFIELD RD | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358258 | 418014 | 400 | 7.621 | 5.1986 | 7.8902 | 30.7263 | 13.683 | 9.8342 | 7.8902 | 5.1053 | 5.1053 | Offer signed, return on 14/03/23
WOODHILL LANE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343294 | 463785 | 400 | 4.5726 | 1.7595 | 2.7595 | 11.9837 | 4.6774 | 3.4275 | 2.7595 | 1.5151 | 2.7595 | Data submitted, clock start due 02/03/2023
WOODHOUSE PARK | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 382132 | 386340 | 630 | 12.0031 | 2.3233 | 5.8233 | 4.38 | 1.6977 | 1.4038 | 4.38 | 1.4344 | 0.86929 | Offer now with ENW, due to be signed 16/08/2023
WOODLEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393116 | 392019 | 400 | 7.621 | 10.8815 | 15.5185 | 16.9459 | 2.79 | 2.0052 | 15.5185 | 1.0921 | 0 | Offer signed, returned on 18/04/23
WOOLFOLD | 11 | BURY | BURY | KEARSLEY | 378874 | 411666 | 630 | 12.0031 | 10.5704 | 14.5704 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed, returned on 18/04/23
WORDSWORTH ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370709 | 410873 | 400 | 4.5726 | 8.8915 | 13.5285 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed, returned on 18/04/23
WORSLEY MESNES | 6.6 | WIGAN | WIGAN | KIRKBY | 357435 | 403977 | 630 | 7.2019 | 5.9029 | 12.4343 | 26.1692 | 10.8598 | 7.9236 | 12.4343 | 7.7377 | 8.7753 | Data submitted for next PP. Awaiting clock start date
WRIGHTINGTON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 353466 | 413290 | 400 | 7.621 | 7.8902 | 7.8902 | 30.4446 | 14.3928 | 10.5469 | 7.8902 | 5.1053 | 5.1053 | Offer signed, return on 14/03/23
YEALAND | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351537 | 475934 | 630 | 12.0031 | 0.90817 | 8.9082 | 12.8478 | 12.8478 | 12.8478 | 8.9082 | 0 | 0 | Awaiting payment for Hutton schemes

## 5) BSP Headroom Data
BSP Headroom
BSP | Voltage (kV) | BCA Group (GSP) | BSP Coordinates |  | Demand Headroom (MW) |  | Generation Headroom - N-0 -(MW) |  | Battery Storage Headroom N-0 -(MW)
|  |  | Easting | Northing | Firm | Non Firm | Inverter Based | Synchronous
ADSWOOD | 33 | BREDBURY | 389188 | 388310 | 58.3982 | 76.3982 | 142.4601 | 45.7788 | 76.3982 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39156%2C-2.16403z=20?hl=en | Offer signed, returned on 18/04/23
AGECROFT | 33 | KEARSLEY | 380345 | 401831 | 17.568 | 29.568 | 91.3244 | 26.7584 | 29.568 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51279%2C-2.29754z=20?hl=en | Offer signed, returned on 18/04/23
ALTRINCHAM | 33 | CARRINGTON | 376380 | 389012 | 58.2632 | 76.2632 | 149.5819 | 50.4027 | 76.2632 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39778%2C-2.35667z=20?hl=en | N/A
ATHERTON | 33 | KEARSLEY | 366150 | 402088 | 22.6446 | 22.6446 | 129.4134 | 28.3425 | 22.6446 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51405%2C-2.51233z=20?hl=en | Offer signed, returned on 18/04/23
BARROW | 33 | HARKER | 319709 | 470489 | 42.482 | 80.482 | 72.7659 | 13.2009 | 72.7659 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.12391%2C-3.23018z=20?hl=en | Offer signed, returned on 11/04/23
BARTON | 33 | CARRINGTON | 376758 | 397174 | 49.9551 | 71.9503 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47087%2C-2.35076z=20?hl=en | N/A
BELFIELD | 33 | ROCHDALE | 391033 | 413945 | 33.1273 | 33.1273 | 73.628 | 23.8288 | 33.1273 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.62216%2C-2.13727z=20?hl=en | Data submitted, clock started 02/03/2023
BISPHAM | 33 | PENWORTHAM | 332328 | 439711 | 39.0606 | 39.0606 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84897%2C-3.04054z=20?hl=en | Offer signed, return on 14/03/23
BLACKBURN | 33 | PENWORTHAM | 370584 | 429294 | 57.2035 | 57.2035 | 64.1341 | 25.3292 | 57.2035 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.7592%2C-2.44764z=20?hl=en | Offer signed, return on 14/03/23
BLACKPOOL | 33 | PENWORTHAM | 330835 | 435308 | 44.9851 | 62.9851 | 137.5524 | 41.8743 | 62.9851 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80944%2C-3.05179z=20?hl=en | Offer signed, return on 14/03/23
BLOOM ST | 33 | SOUTH MANCHESTER | 384221 | 397717 | 11.6816 | 49.1254 | 140.0495 | 44.5173 | 49.1254 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47593%2C-2.23943z=20?hl=en | Offer now with ENW, due to be signed 16/08/2023
BOLTON | 33 | KEARSLEY | 372255 | 410566 | 26.7905 | 39.4827 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59102%2C-2.42059z=20?hl=en | Offer signed, returned on 18/04/23
BURNLEY | 33 | ROCHDALE | 385569 | 434469 | 71.2544 | 83.3704 | 96.2384 | 38.773 | 83.3704 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80624%2C-2.22125z=20?hl=en | Data submitted, clock started 02/03/2023
BURY | 33 | KEARSLEY | 380272 | 411184 | 36.4219 | 36.4219 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5967%2C-2.29975z=20?hl=en | Offer signed, returned on 18/04/23
BUXTON | 33 | STALYBRIDGE | 407769 | 375476 | 38.8236 | 54.9791 | 61.6707 | 11.1881 | 54.9791 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.27596%2C-1.885z=20?hl=en | N/A
CARLISLE | 33 | HARKER | 338655 | 556583 | 29.5792 | 50.7792 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.8993%2C-2.9589z=20?hl=en | Offer signed, returned on 11/04/23
CARRINGTON BSP | 33 | CARRINGTON | 373110 | 393020 | 23.1872 | 44.1872 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.43349%2C-2.40648z=20?hl=en | N/A
CASTLETON | 33 | ROCHDALE | 388461 | 411290 | 44.1915 | 44.1915 | 103.112 | 38.9934 | 44.1915 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59783%2C-2.17663z=20?hl=en | Data submitted, clock started 02/03/2023
CHADDERTON | 33 | WHITEGATE | 389137 | 403821 | 14.6326 | 20.6326 | 50.1829 | 9.104 | 20.6326 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53127%2C-2.16481z=20?hl=en | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
DROYLSDEN | 33 | STALYBRIDGE | 390140 | 398146 | 46.9283 | 64.9283 | 28.7073 | 5.208 | 28.7073 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4802%2C-2.14954z=20?hl=en | N/A
EGREMONT | 33 | HARKER | 301070 | 513074 | 78.3341 | 86.5929 | 58.9084 | 42.6748 | 58.9084 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.50354%2C-3.52919z=20?hl=en | Offer signed, returned on 11/04/23
FREDERICK RD | 33 | KEARSLEY | 381795 | 399250 | 0 | 26.1172 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49066%2C-2.27698z=20?hl=en | Offer signed, returned on 18/04/23
GOLBORNE | 33 | BOLD | 360607 | 397690 | 48.9018 | 66.9018 | 68.9951 | 12.5168 | 66.9018 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47498%2C-2.59493z=20?hl=en | N/A
GREENHILL | 33 | WHITEGATE | 393262 | 404755 | 28.2673 | 28.2673 | 72.1848 | 20.2969 | 28.2673 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53936%2C-2.10308z=20?hl=en | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
HAZEL GROVE | 33 | BREDBURY | 391313 | 386877 | 42.1126 | 55.5526 | 132.2032 | 37.8951 | 55.5526 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.37854%2C-2.1319z=20?hl=en | Offer signed, returned on 18/04/23
HARTSHEAD-HEYROD | 33 | STALYBRIDGE | 397322 | 399942 | 33.9454 | 95.9454 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49638%2C-2.04169z=20?hl=en | N/A
HUNCOAT | 33 | PADIHAM | 377997 | 431083 | 42.082 | 60.082 | 80.0039 | 23.1447 | 60.082 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.77521%2C-2.33688z=20?hl=en | Data Submitted, clock start due 27/05/23
HYDE | 33 | STALYBRIDGE | 395522 | 395647 | 49.9796 | 49.9796 | 41.3268 | 7.4973 | 41.3268 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.45264%2C-2.07376z=20?hl=en | N/A
KEARSLEY LOCAL | 33 | KEARSLEY | 376355 | 404783 | 19.5916 | 60.3916 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53905%2C-2.35884z=20?hl=en | Offer signed, returned on 18/04/23
KENDAL (PARKSIDE RD) | 33 | HUTTON | 351915 | 491858 | 24.2627 | 42.2627 | 118.3801 | 33.0358 | 42.2627 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.31969%2C-2.74168z=20?hl=en | Awaiting payment for Hutton schemes
LANCASTER | 33 | HEYSHAM | 348644 | 463628 | 19.187 | 19.187 | 25.4976 | 4.6257 | 19.187 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.06622%2C-2.78639z=20?hl=en | Data submitted, clock start due 02/03/2023
LEYLAND | 33 | PENWORTHAM | 354121 | 423373 | 20.3621 | 35.3261 | 124.2442 | 33.3111 | 35.3261 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.70478%2C-2.69663z=20?hl=en | Offer signed, return on 14/03/23
LONGSIGHT | 33 | BREDBURY | 385592 | 396016 | 22.537 | 40.537 | 149.1089 | 39.1363 | 40.537 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.46086%2C-2.21901z=20?hl=en | Offer signed, returned on 18/04/23
LOWER DARWEN | 33 | ROCHDALE | 369695 | 424981 | 2.1176 | 52.1176 | 30.322 | 5.5009 | 30.322 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.72038%2C-2.45999z=20?hl=en | Data submitted, clock started 02/03/2023
LYTHAM | 33 | PENWORTHAM | 335361 | 429316 | 0 | 0 | 19.8677 | 19.8677 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75633%2C-2.98215z=20?hl=en | Offer signed, return on 14/03/23
MACCLESFIELD | 33 | MACCLESFIELD | 392047 | 374564 | 6.9671 | 6.9671 | 10.6707 | 1.9358 | 6.9671 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.26811%2C-2.12063z=20?hl=en | N/A
MOSS NOOK | 33 | SOUTH MANCHESTER | 384073 | 385068 | 30.0481 | 50.4481 | 4.2115 | 1.7299 | 4.2115 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.36201%2C-2.2408z=20?hl=en | Offer now with ENW, due to be signed 16/08/2023
NELSON | 33 | PADIHAM | 385989 | 438643 | 9.2209 | 30.6337 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84299%2C-2.214z=20?hl=en | Data Submitted, clock start due 27/05/23
NEW MILLS | 33 | STALYBRIDGE | 401141 | 383916 | 21.9219 | 21.9219 | 53.1931 | 53.1931 | 21.9219 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.35237%2C-1.9844z=20?hl=en | N/A
ORRELL | 33 | KIRKBY | 352784 | 404565 | 13.0246 | 58.0246 | 123.8375 | 47.7854 | 58.0246 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5356%2C-2.71374z=20?hl=en | Data submitted for next PP. Awaiting clock start date
PADIHAM | 33 | PADIHAM | 378571 | 433224 | 18.917 | 52.7788 | 135.9868 | 33.8257 | 52.7788 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79502%2C-2.32919z=20?hl=en | Data Submitted, clock start due 27/05/23
PEEL | 33 | PENWORTHAM | 335644 | 432080 | 2.1727 | 2.1727 | 2.4151 | 2.4151 | 2.1727 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.78114%2C-2.9776z=20?hl=en | Offer signed, return on 14/03/23
PENRITH | 33 | HUTTON | 349996 | 530398 | 35.2918 | 41.11 | 77.7553 | 40.7058 | 41.11 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66637%2C-2.77723z=20?hl=en | Awaiting payment for Hutton schemes
PRESTON EAST | 33 | PENWORTHAM | 356774 | 432942 | 2.1449 | 2.1449 | 10.6707 | 1.9358 | 2.1449 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79104%2C-2.6584z=20?hl=en | Offer signed, return on 14/03/23
RED BANK | 33 | WHITEGATE | 384542 | 399276 | 56.3509 | 74.6472 | 145.8409 | 40.1783 | 74.6472 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49001%2C-2.23427z=20?hl=en | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
RIBBLE | 33 | PENWORTHAM | 351794 | 429241 | 76.7926 | 112.7926 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75725%2C-2.73184z=20?hl=en | Offer signed, return on 14/03/23
ROCHDALE CENTRAL | 33 | ROCHDALE | 389111 | 413393 | 47.0743 | 59.0743 | 94.6521 | 42.0053 | 59.0743 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61653%2C-2.16602z=20?hl=en | Data submitted, clock started 02/03/2023
ROSSENDALE | 33 | PADIHAM | 380261 | 422010 | 38.0078 | 52.0061 | 125.7655 | 59.3504 | 52.0061 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.69402%2C-2.30041z=20?hl=en | Data Submitted, clock start due 27/05/23
ROYTON | 33 | WHITEGATE | 392426 | 407533 | 20.0676 | 97.0462 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56464%2C-2.11572z=20?hl=en | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
SALE | 33 | CARRINGTON | 378726 | 392892 | 25.8239 | 25.8239 | 78.4545 | 49.8062 | 25.8239 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42581%2C-2.31835z=20?hl=en | N/A
SANDGATE | 33 | HARKER | 321492 | 468870 | 42.482 | 80.482 | 126.5341 | 22.9553 | 80.482 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.10982%2C-3.20288z=20?hl=en | Offer signed, returned on 11/04/23
SHAP | 33 | HUTTON | 356910 | 513357 | 35.2918 | 41.11 | 77.7553 | 77.7553 | 41.11 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.51358%2C-2.66756z=20?hl=en | Awaiting payment for Hutton schemes
SIDDICK | 33 | HARKER | 300332 | 530823 | 41.2629 | 85.3629 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.64948%2C-3.51144z=20?hl=en | Offer signed, returned on 11/04/23
SKELMERSDALE | 33 | WASHWAY FARM | 347172 | 407455 | 40.0837 | 40.0837 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56076%2C-2.79859z=20?hl=en | N/A
STAINBURN | 33 | HARKER | 302535 | 529330 | 41.2629 | 85.3629 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66252%2C-3.54717z=20?hl=en | Offer signed, returned on 11/04/23
STRETFORD | 33 | SOUTH MANCHESTER | 380069 | 395104 | 14.5774 | 61.2042 | 131.4503 | 34.0704 | 61.2042 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4523%2C-2.30113z=20?hl=en | Offer now with ENW, due to be signed 16/08/2023
STUART ST | 33 | STALYBRIDGE | 387247 | 398875 | 19.1611 | 44.6611 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.48612%2C-2.19476z=20?hl=en | N/A
THORNTON | 33 | STANAH | 334559 | 443368 | 13.6023 | 25.6023 | 45.5281 | 12.9695 | 25.6023 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.8709%2C-3.00229z=20?hl=en | N/A
ULVERSTON | 33 | HARKER | 327495 | 477808 | 50.2962 | 50.2962 | 70.0323 | 28.1239 | 50.2962 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.1907%2C-3.11215z=20?hl=en | Offer signed, returned on 11/04/23
VERNON PARK | 33 | BREDBURY | 391131 | 390929 | 19.1307 | 19.1307 | 107.1146 | 19.4323 | 19.1307 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.41552%2C-2.13492z=20?hl=en | Offer signed, returned on 18/04/23
WEST DIDSBURY | 33 | SOUTH MANCHESTER | 382900 | 393269 | 15.5488 | 52.0488 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42927%2C-2.25292z=20?hl=en | Offer now with ENW, due to be signed 16/08/2023
WESTHOUGHTON | 33 | KEARSLEY | 365831 | 407025 | 38.4699 | 38.4699 | 41.6268 | 7.5518 | 38.4699 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.55846%2C-2.51787z=20?hl=en | Offer signed, returned on 18/04/23
WIGAN | 33 | KIRKBY | 358343 | 404626 | 5.9029 | 68.9029 | 113.1896 | 42.027 | 68.9029 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53645%2C-2.62967z=20?hl=en | Data submitted for next PP. Awaiting clock start date
WRIGHTINGTON | 33 | PENWORTHAM | 354460 | 413610 | 7.8902 | 7.8902 | 30.7263 | 14.2336 | 7.8902 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61411%2C-2.70439z=20?hl=en | Offer signed, return on 14/03/23

## 6)Transmission Capacity - App G
Appendix G Summary
GSP / Site |  | Capacity of Connected & Contracted Connections (MW) |  |  |  | Materiality Headroom (Part 5) (MW) | Materiality Status | Capacity in Project Progression / Modification Application | Total Aggregated Developer Capacity Limit(MW) | Transmission FL Headroom (kA) | Project Progression Update
|  | Part 1 | Part 2 | Part 3 | Part 4
BOLD* | BOLD | 25.1 | 50.4 | 0 | 0 | 0 | A | N/A | 75.5 | 0 | N/A
BREDBURY | BREDBURY | 10.1 | 134.1 | 0 | 7.6 | 0 | C | 0 | 151.8 | 3 | Offer signed, returned on 18/04/23
CARRINGTON | CARRINGTON | 105 | 94 | 0 | 0 | 139 | A | 0 | 338 | 5.13 | N/A
HARKER | HARKER | 765.4 | 88 | 0 | 152.9 | 0 | C | 0 | 1006.3 | 0 | Offer signed, returned on 11/04/23
HUTTON | HUTTON | 47.9 | 0 | 0 | 53 | 63 | C | 151 | 163.9 | 0 | Awaiting payment for Hutton schemes
HEYSHAM | HEYSHAM | 292.6 | 0 | 109 | 154.4 | 0 | C | 172 | 556 | 0 | Data submitted, clock start due 02/03/2023
KEARSLEY | KEARSLEY | 57.9 | 264.7 | 11 | 0 | 0 | C | 0 | 333.6 | 0 | Offer signed, returned on 18/04/23
KIRKBY | KIRKBY | 6 | 146.4 | 0 | 70 | 0 | B | 110.7 | 222.4 | 3 | Data submitted for next PP. Awaiting clock start date
MACCLESFIELD | MACCLESFIELD | 27.9 | 20 | 0 | 0 | 50 | A | 0 | 97.9 | 2.57 | N/A
PADIHAM | PADIHAM | 35.5 | 135.1 | 219.9 | 0 | 13.5 | B | 174.9 | 404 | 1.55 | Data Submitted, clock start due 27/05/23
PENWORTHAM | PENWORTHAM | 187.9 | 601.1 | 67.6 | 213.2 | 0 | C | 0 | 1069.8 | 9.21 | Offer signed, return on 14/03/23
ROCHDALE | ROCHDALE | 204.1 | 217.5 | 65 | 0 | 50 | C | 109 | 586.6 | 2.62 | Data submitted, clock started 02/03/2023
SOUTH MANCHESTER | SOUTH MANCHESTER | 22.2 | 81.3 | 0 | 372.1 | 0 | C | 0 | 475.6 | 3 | Offer now with ENW, due to be signed 16/08/2023
STALYBRIDGE | STALYBRIDGE | 58.3 | 216.8 | 0 | 0 | 38.2 | A | 0 | 313.3 | 0.818 | N/A
STANAH | STANAH | 195.9 | 112.5 | 0 | 0 | 41 | A | 0 | 349.4 | 3.01 | N/A
WASHWAY FARM | WASHWAY FARM | 7.9 | 101.2 | 0 | 70 | 0 | B | 0 | 179.1 | 3.275 | N/A
WHITEGATE | WHITEGATE | 32 | 219.8 | 0 | 0 | 5.1 | A | 90 | 256.9 | 3.09 | Data submitted, clock start 02/03/2023 (PP Triggered due to Appendix E on Hough Ln BESS 90MW)
Process |  |  | Parts 1 - 5 |  |  |  |  | Materiality Status
The Appendix G process aims to improve on the Statement of Works process by reducing timescales and facilitating greater transparency to the customer. Seventeen of ENWLs twenty GSPs have already converted to the Appendix G process and work is in progress to convert the three remaining sites. The above table summarises the Appendix G results of the GSPs which have already been converted from the Statement of Works process. Sites marked with an asterisk (*) are connected to the transmission network through the distribution network operated by SP Energy Networks. Appendix G submissions for these sites are made by SP Energy Networks on behalf of Electricity North West. For Further information on how to interpret the information presented in this table please refer to the user guide embedded within the first tab of this workbook. |  |  | Appendix G consists of 5 parts: • Part 1 – Existing power stations already connected to our network. • Part 2 – Power stations connected or contracted to connect to our network for which site specific requirements will apply e.g. power factor and controllability. • Part 3 – Power stations connected or contracted to connect to our network for which interim restrictions on availability will apply. Site specific requirements e.g. power factor and controllability, will also apply. • Part 4 – Power stations contracted to connect to our network which are unable to connect until transmission works have been completed. • Part 5 – Materiality headroom. This is a figure, determined by the transmission system operator, representing the available thermal capacity at the transmission system interface before a Modification Application is triggered. |  |  |  |  | To aid understanding we have given each GSP a materiality status. The three status are: A. The latest Appendix G return indicates that there is spare transmission system capacity at this location. B. There is insufficient capacity to accommodate any further sites without undertaking transmission system work. To identify the scope of these works a Modification Application will be required. C. There is insufficient capacity to accommodate any further connections without undertaking work on the transmission system. These works have already been identified and there are sites in project progression. New sites may still require a new Modification Application.